## HSC-VS
SMARTEMP PRODUCT SELECTION CALCULATOR
Helical Vari-Swirl Diffuser [HSC-VS DN355]
Project: | <Project Name>
| Inputs | [6 empty] | Detailed Selection | [12 empty] | v 4.1 [01/2026]
See to 'Notes' worksheet for guide on starting a selection | [7 empty] | Discharge Pattern |  | 4 Way (360°) |  |  | (see 'Notes' worksheet (Row 94) for discharge direction recommendations) | [8 empty] | Specific Airflow Rate (heating) | 5 | L/s/m2 | 2 to 10 L/s/m2 (default 5 L/s/m2)
| Design Airflow Rate | 100 | max 250 L/s | [L/s] | [m³/h]
|  | = 360 | m³/h | [5 empty] | ADPI ≥ | 90% |  | default ≥ 90%
| VAV (turndown to) | 30% | default 30%; min recommended 15%
|  | = 30 | L/s |  |  |  |  | Draught Rating & Heating
| Diffuser Design Static Pressure | 40 | Pa default 30 Pa (max 50 Pa)
Average Diffuser Coverage (Rows 50-52)
|  | Motorised Pressure Control Damper (DMPC) | [5 empty] | OR |  | coverage = 5.9 m
|  | DMPC requires VSC (DMPC stand-alone operation planned for mid-2026) | [6 empty] | Manual Coverage Distance | 6 | m | (see 'Coverage' in Layout Diagram below)
[8 empty] | OR |  | = specfic airflow rate: 2.9 L/s/m²
| ΔT (cooling) | -12 | K -8 to -16 K (default -12 K) | [5 empty] | Specific Airflow Rate | 2.6 | L/s/m² | ≤ 30 L/s/m²
|  |  | use -8 K for 0 K to -8 K | [6 empty] | average diffuser coverage 'C': 5.9 m
| Diffuser Height | 2.7 | m 2 to 5 m | [5 empty] | Room Temperature (draught rating) | 23 | °C | 20 °C to 26 °C (default 23 °C)
| Minimum Damper % at Design Airflow | 60% | default 60%; min recommended 50% | [5 empty] | Diffuser Location | Closed Ceiling |  | Freely Suspended (≥ 600 mm below ceiling)
[9 empty] | % Low Level Return (heating) | 0% |  | 0% to 100% (default 0%)
Related Products | [7 empty] | Thermal Comfort Guide
Vari-Smart® Controller: | optional controller for optimised AHU control and interfacing; available through Fusion Modulair® | [6 empty] | ADPI ≥ 95%; ṽ ≤ 0.20 m/s: | Premium comfort, sedentary activity, such as in auditoria.
Smartemp HSC-FD: | fixed aperture ceiling swirl - VAV optimised | [6 empty] | ADPI ≥ 90%; ṽ ≤ 0.25 m/s: | High comfort near-sedentary activity, such as in board rooms, high end offices and libraries.
Smartemp HSC-AD: | adjustable direction ceiling swirl | [6 empty] | ADPI ≥ 80%; ṽ ≤ 0.29 m/s: | Good comfort near sedentary activity, such as open-plan offices and meeting rooms.
[8 empty] | ADPI ≥ 70%; ṽ ≤ 0.33 m/s: | Standard comfort medium activity, such as in transient spaces, retail and lobbies.
| SMARTEMP HSC-VS- |  |  |  | D0 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | D9 | D10 | Key: | Suitable | Not Suitable | Warning | Warning
Airflow | Airflow @ 100% Damper and 40 Pa |  |  | [L/s] | 254 | 213 | 179 | 157 | 131 | 116 | 97 | 79 | 69 | 60 | 51
| Selected Design Airflow |  |  | [L/s] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Selected Design Static Pressure |  |  | [Pa] | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | ¹ Motorised pressure control damper - static pressure controlled to ≤ 50 Pa
| Damper Position at 100 L/s and 40 Pa |  |  |  | 27% | 34% | 44% | 55% | 67% | 78% | - | - | - | - | -
| Static Pressure @ Design Airflow & 100% Damper |  |  | [Pa] | 6.2 | 8.8 | 12.4 | 16.3 | 23.1 | 29.5 | 42.5 | 64.1 | 84.9 | 112.6 | 156.4
Airflow - VAV | Selected Turndown to % |  |  |  | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30%
| Selected Min Airflow (Turndown To) |  |  | [L/s] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Min Permissible % Turndown to |  |  |  | 22% | 18.5% | 15.5% | 13.6% | 11.4% | 10.1% | 10% | 10% | 10% | 10% | 10% | [5 empty] | `
| Min Permissible Airflow |  |  | [L/s] | 22 | 18.5 | 15.5 | 13.6 | 11.4 | 10.1 | 10 | 10 | 10 | 10 | 10
Heating | Max Recommended Heating ΔT (Centre Zone) |  |  | [K] | 8.3 | 9.4 | 10.4 | 11.2 | 12.1 | 12.9 | 13.7 | 14.6 | 15 | 15 | 15
| Max Recommended Heating ΔT (Perimeter) |  |  | [K] | 5.6 | 6.2 | 6.9 | 7.4 | 8.1 | 8.6 | 9.1 | 9.7 | 10 | 10.4 | 10.7
Distances & Layout | Max Coverage 'Cmax' (for Centre Zones) |  |  | [m] | 8.4 | 8.5 | 8.7 | 8.8 | 9.2 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3
| Max Coverage 'Cmax' (for Perimeter Zones) |  |  | [m] | 7.5 | 7.6 | 7.8 | 8 | 8.3 | 8.6 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3
| Min Coverage 'Cmin' |  |  | [m] | 2.3 | 2.3 | 2.4 | 2.4 | 2.4 | 2.5 | 2.6 | 2.7 | 2.9 | 3.1 | 3.4
| Min Recommended Diffuser Height |  |  | [m] | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.3 | 2.3 | 2.3 | 2.3
Comfort | Mean Room Air Velocity |  |  | [m/s] | 0.11 | 0.11 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.13 | 0.13 | 0.13 | 0.14 | Comfort criteria for specific flowrate of 2.9 L/s/m² (average diffuser spacing of 5.9 m) & room temperature of 23°C
| Mean Draught Rating |  |  | DR | 8.8% | 9% | 9.3% | 9.5% | 9.8% | 10.1% | 10.6% | 11.1% | 11.6% | 12.1% | 12.7%
| Mean PPD |  |  |  | 5.6% | 5.7% | 5.7% | 5.8% | 5.9% | 6% | 6.2% | 6.4% | 6.6% | 6.7% | 7%
| Satisfies PPD Category |  |  | ISO7733 | A | A | A | A | A | B | B | B | B | B | B
| ¦PMV¦ |  |  | ISO7730; ASHRAE Std 55 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.3 | < 0.3 | < 0.3
350 mm High-Profile Connection Box | Spigot | Nominal Spigot Diameter |  | [mm] | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | See 'Connection Box Details' worksheet for drawings and dimensions
|  | Static Pressure (Spigot) |  | [Pa] | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 47 | 68.6 | 89.4 | 117.1 | 160.9
|  | Total Pressure (Spigot) |  | [Pa] | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 53.2 | 74.8 | 95.6 | 123.3 | 167.1 | Acoustic values valid for diffuser including side-entry connection box with the recommended spigot size. See 'Connection Box Details' worksheet. * Sound Pressure Level (NC) based on 10 dB(A) noise absoption. See 'Notes' worksheet row 16.
| Acoustic | Sound Power Level |  | [dB(A)] | 41.8 | 41.3 | 40.7 | 40 | 39.1 | 38.5 | 39.3 | 60.2 | - | - | -
|  | Sound Pressure Level * |  | [NC] | 26.8 | 26.3 | 25.7 | 25 | 24.1 | 23.5 | 24.3 | 45.2 | - | - | -
250 mm Medium-Profile Connection Box | Spigot | Nominal Spigot Diameter |  | [mm] | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200
|  | Static Pressure (Spigot) |  | [Pa] | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 48.7 | 70.3 | 91.2 | 118.8 | 162.6
|  | Total Pressure (Spigot) |  | [Pa] | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 55.2 | 76.9 | 97.7 | 125.4 | 169.2
| Acoustic | Sound Power Level |  | [dB(A)] | 43.3 | 42.7 | 42.1 | 41.4 | 40.6 | 40 | 40.7 | 61.6 | - | - | -
|  | Sound Pressure Level * |  | [NC] | 28.3 | 27.7 | 27.1 | 26.4 | 25.6 | 25 | 25.7 | 46.6 | - | - | -
200 mm Low-Profile Connection Box | Spigot | Nominal Spigot Diameter |  | [mm] | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250
|  | Static Pressure (Spigot) |  | [Pa] | 57.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 50 | 71.6 | 92.4 | 120.1 | 163.9
|  | Total Pressure (Spigot) |  | [Pa] | 63.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 55.7 | 77.4 | 98.2 | 125.9 | 169.6
| Acoustic | Sound Power Level |  | [dB(A)] | 47.1 | 46.5 | 45.9 | 45.2 | 44.4 | 43.8 | 44.6 | 65.4 | - | - | -
|  | Sound Pressure Level * |  | [NC] | 32.1 | 31.5 | 30.9 | 30.2 | 29.4 | 28.8 | 29.6 | 50.4 | - | - | - | Refer to 'Notes' worksheet for Selection help
Product Selection & Code Generator
| Door Setting |  | Diffusers are shipped with their VAV dampers set to D0. Door settings need not be specified. Suitable adjustment to the door setting is recommended by the diffuser microprocessor during on-site air balancing. | [11 empty] | * indicates standard/default option
| Discharge Direction |  | 4 Way (360°) selected in cell M9. Shipped door setting is 4-way; adjustable on site to 2-way or 3-way | [11 empty] | - see cell M9
| Face Shape |  |  | □ 595 mm square face * |  | custom square face (□495 to □603 mm) |  |  | ⌀ 600mm circular face - for freely suspended applications only | [5 empty] | □ 595 mm square face
| Optional On-board Sensors (Plug-in) |  | IAQ sensor (select one) |  |  | PIR | [8 empty] | Room Temperature, Supply Temperature, and Supply Pressure sensors come standard.
|  |  | Plug-in Options: | CO2 & RH VOC
| Optional Wall Sensor |  | No Wall-Stat * |  |  |  | Push button Wall-Stat with Room Temp |  | Touch Screen Wall-Stat with Room Temp (Available mid-2026)
[9 empty] | Options: | CO2 & RH | VOC
| Face Colour |  |  | RAL9003* (signal white) |  | RAL9005 (jet black) |  | other | [6 empty] | Powder coated
| Connection Box |  | Side entry spigot |  | Top entry spigot |  | Side entry spigot with Gravity Pressure Relief Damper |  |  |  | Side entry spigots with Motorised Supply Source Damper |  |  |  | Contact SMARTEMP for dimensions of the GPRD and MPCD spigot variants
| Height |  | 250 mm high box (default) |  |  | 350 mm high box |  | 200 mm high box |  | bespoke
| Spigot Size |  |  | DN200 (default) |  | DN150 |  | DN250 |  | bespoke spigot |  |  |  |  | DN200 mm (default)
| Options |  | Foam* |  | Sheetmetal |  | R1 Insulation* |  | R2 Insulation | [5 empty] | Foam box with R1 insulation
| System Setup |  | Stand-Alone: Each HSC-VS diffuser is suitable to operate stand-alone (requires 24 VDC power supply).
| Stand-Alone or Networked (see Notes for more detail) |  | • No Wall-Stat: Diffuser commissioning and air balancing requires micro-USB connection of a laptop, programmed with commissioning tools, to the diffuser hub. | [11 empty] | See Notes for more detail
• Wall Stat: An optional wall-stat (push-button or touchscreen) wired to the diffuser allows setpoint adjustment by the user, and direct diffuser commissioning and air balancing.
• BMS Linked: A Modbus RS485 comms chain may optionally link stand-alone HSC-VS diffusers (with or without a wall-stat) to a BMS / central controller (by others) to allow diffuser sensors to be monitored and/or set-points to be changed remotely, and to provide laptop network access for commissioning and air balancing via a Smartair Commissioning App.
Networked: A Modbus RS465 comms chain is required to link HSC-VS diffusers as for “BMS Linked” operation above (with or without wall-stat); plus AHU/FCU control and system optimisation by the Vari-Swirl diffuser system via one of two options:
• Central Location by others: a third-party BMS / central controller is supplied and programmed by others to provide simplified AHU/FCU control.
• Vari-smart controller: a VSC (optionally connected to a BMS) is available from Fusion Modulair™, pre-programmed to aggregate HSC-VS preferences and dynamically reset and optimise requests for AHU/FCU
| Order Code |  | SMARTEMP HSC-VS-DN355-S595-KF250R1-SD200-RAL9003-SE-D0-SC-W0 | [11 empty] | more detailed options and information available in the HSC-VS product brochure
| Description |  | HSC-VS Diffuser • Recommended D5 door setting (adjusted on-site) • 4 Way (360°) discharge • □ 595 mm square face • Powder coated to RAL9003 |  |  |  | Connection Box Details • 250 mm high box (default) • Foam box with R1 insulation • DN200 mm (default) side entry spigot • No pressure damper |  |  | Standard On-Board Sensors • Supply Temperature • Room Temperature • Supply Pressure Optional On-board sensors • IAQ Sensor (CO₂ + RH) |  | HMI Options • No wall stat selected • Room Temp |  |  | go to 'HSC-VS Selection Summary' for a printable summary of the selection
[7 empty] | click to see product on smartair.asia | [11 empty] | Copyright © 2026 SMARTAIR DIFFUSION
26
Group Box 43
Group Box 1236
Group Box 1325
Group Box 1350
Layout Diagram
sdf
Group Box 2061
Group Box 58
Group Box 2791
Group Box 2800
Group Box 3531

## Equations (hidden)
Units
| Unit Type | 1 | [L/s] | L/s
| Unit Multiplier | 1 | L/s/m²
| Max Airflow | 250
| Airflow Rate | 100
| Converted Flowrate | = 360 | m³/h
Input Values
| Neck Size |  |  | mm | [6 empty] | Max Airflow
| Airflow Rate - Converted | 100 |  | L/s | [6 empty] | Max Recommended Airflow (L/s)
| VAV | 0.3 |  | % | [6 empty] | Min Airflow (L/s)
| Diffuser Static Pressure | 40 | [8 empty] | Min P Airflow
| MPCD | FALSE
| dT (cooling) | -12 |  | K | [6 empty] | Min % Airflow
| Minimum Damper Percent at Design | 60%
| Room Height | 2.7 |  | m | [6 empty] | Min Permissible % TD to
| Discharge Direction | 4 Way (360°) | 4w | [7 empty] | Max Total Pressure (Pa)
| Spec Airflow Rate | 2.6 |  | L/s/m2
| ADPI | 90% | [8 empty] | Sound Power Level (dBA)
| perforated plate | FALSE | [8 empty] | Sound Pressure Level (NC)
| Low level return | 0 | [8 empty] | Max Permissible ΔT (heating) (K)
| freely suspended | 1
| Room Temp | 23 |  | C
| Diffuser dist setting | 1
| manual diffuser dist | 6 |  | m | [6 empty] | H_min (m)
C_min (m)
| Input Pre Calcs | [9 empty] | C_max (m)
| Neck Size | 355
| VAV | 0.3
| Max Static Pressure | 40 |  | Pa
| MPCD Static | 50 |  | Pa
| Turndown Flowrate | 30
| dT (cooling) | 12 | for @ velocity use '-8' for values 0 and -8 K
| Room Height | 2.7
| Discharge Direction | 4
| Spec Airflow Rate for heating | 2.9
| ADPI | 90
| Local Velocity | 0.25
| V_turndown | 30 |  | v_td=afr*vav
| Low Level Return | 1
| free susp | FALSE
| Free Susp (heat) | 1
| Free Susp (Hmin) | 1
| Free susp (Cmin) | 1
| Free Susp (Cmax) | 1
| 2-Way 180 deg | 1
| Flowrate 30Pa Equiv | 86.6025 | (for damper positioning)
Cmin Table
Target Q''
| H | ax | ^b | Q''
| 2.7 | 4510 | 2.2693 | 194.0536
| 4 | 3884 | 2.2426 | 173.4201
| 10.0001 | 3435 | 2.2754 | 146.5546
|  | Ax | ^b
| 2.7 | 235.858 | -0.20897 | 191.6493 | W/m2
v'
| v' & Vmax | 15.9708
| v' & Vmin | 19.9708
| v'' +correction factor | 4
Cmax Constants
f_TD
| TD | Factor
| 100% | 1
| 30% | 0.535
| Absolute Min | 0.535
| Factor | 0.535 | f_TD
f_Pressure
| Pressure | Factor
| 30 | 0.75
| 5 | 1
Specific Flow Rate
| Centre | (equiv. FD min)
| adpi | v' (L/s/m2) @ -12
| 95% | 1.0121 | [6 empty] | 0.95 | 0.9 | 0.8 | 0.7
| 90% | 0.80827 | [6 empty] | 1.27 | 1 | 0.7 | 0.5
| 85% | 0.6503 | [6 empty] | 1.2564 | 1.0245 | 0.68304 | 0.50459
| 80% | 0.53818
| 70% | 0.45147
| v' (selected) | 0.80827
| Perimeter | (equiv. FD min)
| adpi | v' (L/s/m2) @ -12
| 95% | 1.27
| 90% | 1
| 85% | 0.80827
| 80% | 0.66
| 70% | 0.47 | [5 empty] | 0.95 | 0.9 | 0.85 | 0.8 | 0.75 | 0.7 | 0.65
| v' (selected) | 1 | [9 empty] | 0.7 |  | 0.5
Cmax-Perimeter Zone Table
| adpi | v' @Vmax | v' @ Vmin |  | Hfactor @ Vmax | Hfactor @ Vmin
| 95% | 0.955 | 1.27 |  | 5.317 | 4.4309
| 90% | 0.75 | 1 |  | 6 | 5
| 85% | 0.60762 | 0.80827 |  | 6.6828 | 5.5685
| 80% | 0.5 | 0.66 |  | 7.3659 | 6.1383
| 70% | 0.35 | 0.47 |  | 8.7318 | 7.2765
| v' & Vmax | 0.75 |  | at ADPI | 6 | factor * room height
| v' & Vmin | 1 |  |  | 5
Cmax-Centre Zone Table
| adpi | v' @Vmax | v' @ Vmin |  | Hfactor @ Vmax | Hfactor @ Vmin
| 95% | 0.75963 | 1.0121 |  | 5.317 | 4.4309
| 90% | 0.60762 | 0.80827 |  | 6 | 5
| 85% | 0.48872 | 0.6503 |  | 6.6828 | 5.5685
| 80% | 0.40294 | 0.53818 |  | 7.3659 | 6.1383
| 70% | 0.33072 | 0.45147 |  | 8.7318 | 7.2765
| v' & Vmax | 0.60762 |  | at ADPI | 6 | factor * room height
| v' & Vmin | 0.80827 |  |  | 5
COVERAGE AND RADIUS - multipliers (discharge patttern)
| R multiplier | 0.5
| Area multiplier | 4 | A= M*R^2
| R to Coverage Conversion | 2
| Area multiplier from C | 1 | A= M * C^2
| Box/Perf Pressure Loss | Loss vs Box/Board Pressure
DN250
| Coefficient | 0.011
| Pressure Loss | 1.21
Damper Acoustic Eqn
| Pa | x3 | x2 | x | c
| 60 | -1.0427 | 1.261 | 3.0318 | 44.286
| 20 | 59.824 | -103.6 | 50.612 | 25.212
Theoretical Flow Rates
| L | 24.62 | L/s
| S | 16.8 | L/s
| I | 10.2 | L/s
Face Loss Coefficients
| a | 0.0015617 | v^2
| b | -0.28876 | v^1
| c | 16.1751 | c
| lim | 110 | Limit where face has no effect
MPCD Adjustments
Throttle Pressure Ratio
| 355 | [70 empty] | DN500
| D0 | [6 empty] | D1 | [6 empty] | D2 | [6 empty] | D3 | [6 empty] | D4 | [6 empty] | D5 | [6 empty] | D6 | [5 empty] | D7 |  |  |  |  | D8 | [5 empty] | D9 | [5 empty] | D10
| Spigot Dia | 300
| Data and Configuration | [6 empty] | Data and Configuration | [6 empty] | Data and Configuration | [6 empty] | Data and Configuration | [6 empty] | Data and Configuration | [6 empty] | Data and Configuration | [6 empty] | Data and Configuration | [5 empty] | Data and Configuration |  |  |  |  | Data and Configuration | [5 empty] | Data and Configuration | [5 empty] | Data and Configuration
|  | Large | Small | [5 empty] | Large | Small | [5 empty] | Large | Small | [5 empty] | Large | Small | [5 empty] | Large | Small | [5 empty] | Large | Small | [5 empty] | Large | Small |  |  |  |  | Large | Small |  |  |  | Large | Small |  |  |  |  | Large | Small |  |  |  |  | Large | Small
| 4w | 8 | 4 |  |  |  |  | 4w | 6 | 3 |  |  |  |  | 4w | 5 | 2 |  |  |  |  | 4w | 4 | 2 |  |  |  |  | 4w | 3 | 2 |  |  |  |  | 4w | 3 | 1 |  |  |  |  | 4w | 3 | 0 |  |  |  | 4w | 1 | 2 |  |  | 4w | 2 | 0 |  |  |  | 4w | 1 | 1 |  |  |  | 4w | 0 | 2
|  | Y/N | V_theo | [5 empty] | Y/N | V_theo | [5 empty] | Y/N | V_theo | [5 empty] | Y/N | V_theo | [5 empty] | Y/N | V_theo | [5 empty] | Y/N | V_theo | [5 empty] | Y/N | V_theo |  |  |  |  | Y/N | V_theo |  |  |  | Y/N | V_theo |  |  |  |  | Y/N | V_theo |  |  |  |  | Y/N | V_theo
| 4w | TRUE | 274.36 |  |  |  |  | 4w | TRUE | 208.32 |  |  |  |  | 4w | TRUE | 166.9 |  |  |  |  | 4w | TRUE | 142.28 |  |  |  |  | 4w | TRUE | 117.66 |  |  |  |  | 4w | TRUE | 100.86 |  |  |  |  | 4w | TRUE | 84.06 |  |  |  | 4w | TRUE | 68.42 |  |  | 4w | TRUE | 59.44 |  |  |  | 4w | TRUE | 51.62 |  |  |  | 4w | TRUE | 43.8
| 3w | FALSE | 0 |  |  |  |  | 3w | TRUE | 208.32 |  |  |  |  | 3w | TRUE | 166.9 |  |  |  |  | 3w | TRUE | 142.28 |  |  |  |  | 3w | TRUE | 117.66 |  |  |  |  | 3w | TRUE | 100.86 |  |  |  |  | 3w | TRUE | 84.06 |  |  |  | 3w | TRUE | 68.42 |  |  | 3w | TRUE | 59.44 |  |  |  | 3w | TRUE | 51.62 |  |  |  | 3w | TRUE | 43.8
| 2s | FALSE | 0 |  |  |  |  | 2s | FALSE | 0 |  |  |  |  | 2s | TRUE | 166.9 |  |  |  |  | 2s | TRUE | 142.28 |  |  |  |  | 2s | TRUE | 117.66 |  |  |  |  | 2s | TRUE | 100.86 |  |  |  |  | 2s | TRUE | 84.06 |  |  |  | 2s | TRUE | 68.42 |  |  | 2s | TRUE | 59.44 |  |  |  | 2s | TRUE | 51.62 |  |  |  | 2s | TRUE | 43.8
| 2a | FALSE | 0 |  |  |  |  | 2a | FALSE | 0 |  |  |  |  | 2a | TRUE | 166.9 |  |  |  |  | 2a | TRUE | 142.28 |  |  |  |  | 2a | TRUE | 117.66 |  |  |  |  | 2a | TRUE | 100.86 |  |  |  |  | 2a | TRUE | 84.06 |  |  |  | 2a | TRUE | 68.42 |  |  | 2a | TRUE | 59.44 |  |  |  | 2a | TRUE | 51.62 |  |  |  | 2a | TRUE | 43.8
| Select | TRUE | 274.36 | L/s |  |  |  | Select | TRUE | 208.32 | L/s |  |  |  | Select | TRUE | 166.9 | L/s |  |  |  | Select | TRUE | 142.28 | L/s |  |  |  | Select | TRUE | 117.66 | L/s |  |  |  | Select | TRUE | 100.86 | L/s |  |  |  | Select | TRUE | 84.06 | L/s |  |  | Select | TRUE | 68.42 | L/s |  | Select | TRUE | 59.44 | L/s |  |  | Select | TRUE | 51.62 | L/s |  |  | Select | TRUE | 43.8 | L/s
| Data | [6 empty] | Data | [6 empty] | Data | [6 empty] | Data | [6 empty] | Data | [6 empty] | Data | [6 empty] | Data | [5 empty] | Data |  |  |  |  | Data | [5 empty] | Data | [5 empty] | Data
| Loss | 54.5034 | L/s |  |  |  |  | Loss | 23.7931 | L/s |  |  |  |  | Loss | 11.4827 | L/s |  |  |  |  | Loss | 6.7045 | L/s |  |  |  |  | Loss | 3.8195 | L/s |  |  |  |  | Loss | 0 | L/s |  |  |  |  | Loss | 0 | L/s |  |  |  | Loss | 0 | L/s |  |  | Loss | 0 | L/s |  |  |  | Loss | 0 | L/s |  |  |  | Loss | 0 | L/s
| Max Airflow at 30 Pa | 219.8566 | L/s |  |  |  |  | Adj.Flowrate | 184.5269 | L/s |  |  |  |  | Adj.Flowrate | 155.4173 | L/s |  |  |  |  | Adj.Flowrate | 135.5755 | L/s |  |  |  |  | Adj.Flowrate | 113.8405 | L/s |  |  |  |  | Adj.Flowrate | 100.86 | L/s |  |  |  |  | Adj.Flowrate | 84.06 | L/s |  |  |  | Adj.Flowrate | 68.42 | L/s |  |  | Adj.Flowrate | 59.44 | L/s |  |  |  | Adj.Flowrate | 51.62 | L/s |  |  |  | Adj.Flowrate | 43.8 | L/s
| Max Airflow at Design P | 253.8686 | L/s |  |  |  |  | Max Airflow at Design P | 213.0733 | [5 empty] | Max Airflow at Design P | 179.4604 | [5 empty] | Max Airflow at Design P | 156.5491 | [5 empty] | Max Airflow at Design P | 131.4517 | [5 empty] | Max Airflow at Design P | 116.4631 | [5 empty] | Max Airflow at Design P | 97.0641 |  |  |  |  | Max Airflow at Design P | 79.0046 |  |  |  | Max Airflow at Design P | 68.6354 |  |  |  |  | Max Airflow at Design P | 59.6056 |  |  |  |  | Max Airflow at Design P | 50.5759
| data.Pboard | 30 | Pa |  |  |  |  | data.Pboard | 30 | Pa |  |  |  |  | data.Pboard | 30 | Pa |  |  |  |  | data.Pboard | 30 | Pa |  |  |  |  | data.Pboard | 30 | Pa |  |  |  |  | data.Pboard | 30 | Pa |  |  |  |  | data.Pboard | 30 | Pa |  |  |  | data.Pboard | 30 | Pa |  |  | data.Pboard | 30 | Pa |  |  |  | data.Pboard | 30 | Pa |  |  |  | data.Pboard | 30 | Pa
| data.MinFlowrate | 21.9857 | L/s |  |  |  |  | data.MinFlowrate | 18.4527 | L/s |  |  |  |  | data.MinFlowrate | 15.5417 | L/s |  |  |  |  | data.MinFlowrate | 13.5575 | L/s |  |  |  |  | data.MinFlowrate | 11.384 | L/s |  |  |  |  | data.MinFlowrate | 10.086 | L/s |  |  |  |  | data.MinFlowrate | 8.406 | L/s |  |  |  | data.MinFlowrate | 6.842 | L/s |  |  | data.MinFlowrate | 5.944 | L/s |  |  |  | data.MinFlowrate | 5.162 | L/s |  |  |  | data.MinFlowrate | 4.38 | L/s
| Airflow | [6 empty] | Airflow | [6 empty] | Airflow | [6 empty] | Airflow | [6 empty] | Airflow | [6 empty] | Airflow | [6 empty] | Airflow | [5 empty] | Airflow |  |  |  |  | Airflow | [5 empty] | Airflow | [5 empty] | Airflow
| Total Pressure (fully open) | 6.2064 | Pa |  |  |  |  | Total Pressure (fully open) | 8.8105 | Pa |  |  |  |  | Total Pressure (fully open) | 12.42 | Pa |  |  |  |  | Total Pressure (fully open) | 16.3215 | Pa |  |  |  |  | Total Pressure (fully open) | 23.1488 | Pa |  |  |  |  | Total Pressure (fully open) | 29.4906 | Pa |  |  |  |  | Total Pressure (fully open) | 42.4563 | Pa |  |  |  | Total Pressure (fully open) | 64.0848 | Pa |  |  | Total Pressure (fully open) | 84.9109 | Pa |  |  |  | Total Pressure (fully open) | 112.5862 | Pa |  |  |  | Total Pressure (fully open) | 156.3771 | Pa
| Flowrate @ MaxP | 253.8686 | L/s |  |  |  |  | Flowrate @ MaxP | 213.0733 | L/s |  |  |  |  | Flowrate @ MaxP | 179.4604 | L/s |  |  |  |  | Flowrate @ MaxP | 156.5491 | L/s |  |  |  |  | Flowrate @ MaxP | 131.4517 | L/s |  |  |  |  | Flowrate @ MaxP | 116.4631 | L/s |  |  |  |  | Flowrate @ MaxP | 97.0641 | L/s |  |  |  | Flowrate @ MaxP | 79.0046 | L/s |  |  | Flowrate @ MaxP | 68.6354 | L/s |  |  |  | Flowrate @ MaxP | 59.6056 | L/s |  |  |  | Flowrate @ MaxP | 50.5759 | L/s
| V_min | 21.9857 | L/s |  |  |  |  | V_min | 18.4527 | L/s |  |  |  |  | V_min | 15.5417 | L/s |  |  |  |  | V_min | 13.5575 | L/s |  |  |  |  | V_min | 11.384 | L/s |  |  |  |  | V_min | 10.086 | L/s |  |  |  |  | V_min | 10 | L/s |  |  |  | V_min | 10 | L/s |  |  | V_min | 10 | L/s |  |  |  | V_min | 10 | L/s |  |  |  | V_min | 10 | L/s
| Min % turndown to | 21.99% | [5 empty] | Min % turndown to | 18.45% | [5 empty] | Min % turndown to | 15.54% | [5 empty] | Min % turndown to | 13.56% | [5 empty] | Min % turndown to | 11.38% | [5 empty] | Min % turndown to | 10.09% | [5 empty] | Min % turndown to | 10% |  |  |  |  | Min % turndown to | 10% |  |  |  | Min % turndown to | 10% |  |  |  |  | Min % turndown to | 10% |  |  |  |  | Min % turndown to | 10%
| Damper Positions | [6 empty] | Damper Positions | [6 empty] | Damper Positions | [6 empty] | Damper Positions | [6 empty] | Damper Positions | [6 empty] | Damper Positions | [6 empty] | Damper Positions | [5 empty] | Damper Positions |  |  |  |  | Damper Positions | [5 empty] | Damper Positions | [5 empty] | Damper Positions
Airflow 30Pa Equiv
| Damper Pos | Data | [5 empty] | Damper Pos | Data | [5 empty] | Damper Pos | Data | [5 empty] | Damper Pos | Data | [5 empty] | Damper Pos | Data | [5 empty] | Damper Pos | Data | [5 empty] | Damper Pos | Data |  |  |  |  | Damper Pos | Data |  |  |  | Damper Pos | Data |  |  |  |  | Damper Pos | Data |  |  |  |  | Damper Pos | Data
| 100 | 219.8 | [5 empty] | 100 | 184.6 | [5 empty] | 100 | 155.2 | [5 empty] | 100 | 135.7 | [5 empty] | 100 | 113.9 | [5 empty] | 100 | 100.5 | [5 empty] | 100 | 84.6 |  |  |  |  | 100 | 68.4 |  |  |  | 100 | 59.6 |  |  |  |  | 100 | 50.8 |  |  |  |  | 100 | 44.6
| 80 | 206.5 | [5 empty] | 80 | 164.7 | [5 empty] | 80 | 138.2 | [5 empty] | 80 | 119.3 | [5 empty] | 80 | 99.5 | [5 empty] | 80 | 88.7 | [5 empty] | 80 | 74.1 |  |  |  |  | 80 | 62.6 |  |  |  | 80 | 55.7 |  |  |  |  | 80 | 49.7 |  |  |  |  | 80 | 43.7
| 40 | 130.5 | [5 empty] | 40 | 102.1 | [5 empty] | 40 | 79.5 | [5 empty] | 40 | 64.6 | [5 empty] | 40 | 54.3 | [5 empty] | 40 | 47.8 | [5 empty] | 40 | 41.8 |  |  |  |  | 40 | 36.5 |  |  |  | 40 | 33.8 |  |  |  |  | 40 | 31.6 |  |  |  |  | 40 | 29.6
| 20 | 62.7 | [5 empty] | 20 | 48.4 | [5 empty] | 20 | 39.7 | [5 empty] | 20 | 34.2 | [5 empty] | 20 | 31.6 | [5 empty] | 20 | 23.6 | [5 empty] | 20 | 22.4 |  |  |  |  | 20 | 18.2 |  |  |  | 20 | 16.1 |  |  |  |  | 20 | 14.3 |  |  |  |  | 20 | 12.4
| Airflow Limit | [6 empty] | Airflow Limit | [6 empty] | Airflow Limit | [6 empty] | Airflow Limit | [6 empty] | Airflow Limit | [6 empty] | Airflow Limit | [6 empty] | Airflow Limit | [5 empty] | Airflow Limit |  |  |  |  | Airflow Limit | [5 empty] | Airflow Limit | [5 empty] | Airflow Limit
| 100 | 253.8032 | [5 empty] | 100 | 213.1577 | [5 empty] | 100 | 179.2095 | [5 empty] | 100 | 156.6929 | [5 empty] | 100 | 131.5204 | [5 empty] | 100 | 116.0474 | [5 empty] | 100 | 97.6877 |  |  |  |  | 100 | 78.9815 |  |  |  | 100 | 68.8202 |  |  |  |  | 100 | 58.6588 |  |  |  |  | 100 | 51.4996
| 80 | 238.4457 | [5 empty] | 80 | 190.1792 | [5 empty] | 80 | 159.5796 | [5 empty] | 80 | 137.7558 | [5 empty] | 80 | 114.8927 | [5 empty] | 80 | 102.4219 | [5 empty] | 80 | 85.5633 |  |  |  |  | 80 | 72.2843 |  |  |  | 80 | 64.3168 |  |  |  |  | 80 | 57.3886 |  |  |  |  | 80 | 50.4604
| 40 | 150.6884 | [5 empty] | 40 | 117.8949 | [5 empty] | 40 | 91.7987 | [5 empty] | 40 | 74.5937 | [5 empty] | 40 | 62.7002 | [5 empty] | 40 | 55.1947 | [5 empty] | 40 | 48.2665 |  |  |  |  | 40 | 42.1466 |  |  |  | 40 | 39.0289 |  |  |  |  | 40 | 36.4885 |  |  |  |  | 40 | 34.1791
| 20 | 72.3997 | [5 empty] | 20 | 55.8875 | [5 empty] | 20 | 45.8416 | [5 empty] | 20 | 39.4908 | [5 empty] | 20 | 36.4885 | [5 empty] | 20 | 27.2509 | [5 empty] | 20 | 25.8653 |  |  |  |  | 20 | 21.0155 |  |  |  | 20 | 18.5907 |  |  |  |  | 20 | 16.5122 |  |  |  |  | 20 | 14.3183
| Ax^2 | Bx | C |  |  |  |  | Ax^2 | Bx | C |  |  |  |  | Ax^2 | Bx | C |  |  |  |  | Ax^2 | Bx | C |  |  |  |  | Ax^2 | Bx | C |  |  |  |  | Ax^2 | Bx | C |  |  |  |  | Ax^2 | Bx | C |  |  |  | Ax^2 | Bx | C |  |  | Ax^2 | Bx | C |  |  |  | Ax^2 | Bx | C |  |  |  | Ax^2 | Bx | C
| 0 | 1.5038 | -230.53 |  |  |  |  | 0 | 1.005 | -85.528 |  |  |  |  | 0 | 1.1765 | -82.588 |  |  |  |  | 0 | 1.2195 | -65.488 |  |  |  |  | 0 | 1.3889 | -58.194 |  |  |  |  | 0 | 1.6949 | -70.339 |  |  |  |  | 0 | 1.9048 | -61.143 |  |  |  | 0 | 3.4483 | -135.86 |  |  | 0 | 5.1282 | -205.64 |  |  |  | 0 | 18.182 | -823.64 |  |  |  | 0 | 22.222 | -891.11
| 0.00419 | -0.8856 | 84.216 |  |  |  |  | 0.00164 | 0.2012 | 2.3557 |  |  |  |  | 0.00163 | 0.3267 | 3.7306 |  |  |  |  | 0.00142 | 0.4698 | 3.7157 |  |  |  |  | 0.00385 | 0.2931 | 12.738 |  |  |  |  | 0.0046 | 0.3498 | 12.764 |  |  |  |  | 0.0109 | -0.0243 | 21.98 |  |  |  | 0.016 | -0.0567 | 20.704 |  |  | 0.0257 | -0.4753 | 26.684 |  |  |  | 0.0402 | -1.0547 | 33.231 |  |  |  | 0.0737 | -2.5626 | 51.312
| 0 | 0.295 | 1.5044 |  |  |  |  | 0 | 0.3724 | 1.9739 |  |  |  |  | 0 | 0.5025 | 0.0503 |  |  |  |  | 0 | 0.6579 | -2.5 |  |  |  |  | 0 | 0.8811 | -7.8414 |  |  |  |  | 0 | 0.8264 | 0.4959 |  |  |  |  | 0 | 1.0309 | -3.0928 |  |  |  | 0 | 1.0929 | 0.1093 |  |  | 0 | 1.1299 | 1.8079 |  |  |  | 0 | 1.1561 | 3.4682 |  |  |  | 0 | 1.1628 | 5.5814
| Airflow -> Damper | [6 empty] | Airflow -> Damper | [6 empty] | Airflow -> Damper | [6 empty] | Airflow -> Damper | [6 empty] | Airflow -> Damper | [6 empty] | Airflow -> Damper | [6 empty] | Airflow -> Damper | [5 empty] | Airflow -> Damper |  |  |  |  | Airflow -> Damper | [5 empty] | Airflow -> Damper | [5 empty] | Airflow -> Damper
| Airflow Bracket | 2 | [5 empty] | Airflow Bracket | 2 | [5 empty] | Airflow Bracket | 1 | [5 empty] | Airflow Bracket | 1 | [5 empty] | Airflow Bracket | 1 | [5 empty] | Airflow Bracket | 1 | [5 empty] | Airflow Bracket | 0 |  |  |  |  | Airflow Bracket | 0 |  |  |  | Airflow Bracket | 0 |  |  |  |  | Airflow Bracket | 0 |  |  |  |  | Airflow Bracket | 0
| Eqn | 0 | 0.295 | 1.5044 |  |  |  | Eqn | 0 | 0.3724 | 1.9739 |  |  |  | Eqn | 0.00163 | 0.3267 | 3.7306 |  |  |  | Eqn | 0.00142 | 0.4698 | 3.7157 |  |  |  | Eqn | 0.00385 | 0.2931 | 12.738 |  |  |  | Eqn | 0.0046 | 0.3498 | 12.764 |  |  |  | Eqn | 0 | 1.9048 | -61.143 |  |  | Eqn | 0 | 3.4483 | -135.86 |  | Eqn | 0 | 5.1282 | -205.64 |  |  | Eqn | 0 | 18.182 | -823.64 |  |  | Eqn | 0 | 22.222 | -891.11
| Damper Position | 27% | [5 empty] | Damper Position | 34% | [5 empty] | Damper Position | 44% | [5 empty] | Damper Position | 55% | [5 empty] | Damper Position | 67% | [5 empty] | Damper Position | 78% | [5 empty] | Damper Position | 104% |  |  |  |  | Damper Position | 163% |  |  |  | Damper Position | 238% |  |  |  |  | Damper Position | 751% |  |  |  |  | Damper Position | 1033%
| D0 | [6 empty] | D1 | [6 empty] | D2 | [6 empty] | D3 | [6 empty] | D4 | [6 empty] | D5 | [6 empty] | D6 | [5 empty] | D7 |  |  |  |  | D8 | [5 empty] | D9 | [5 empty] | D10
| Acoustic | 20200822_Vari-Swirl_Acoustics.xlsx
| 4w basket Flowrate | 274.36 | [5 empty] | 4w basket Flowrate | 208.32 | [5 empty] | 4w basket Flowrate | 166.9 | [5 empty] | 4w basket Flowrate | 142.28 | [5 empty] | 4w basket Flowrate | 117.66 | [5 empty] | 4w basket Flowrate | 100.86 | [5 empty] | 4w basket Flowrate | 84.06 |  |  |  |  | 4w basket Flowrate | 68.42 |  |  |  | 4w basket Flowrate | 59.44 |  |  |  |  | 4w basket Flowrate | 51.62 |  |  |  |  | 4w basket Flowrate | 43.8
| Loss | 47.6162 | [5 empty] | Loss | 20.4814 | [5 empty] | Loss | 9.2489 | [5 empty] | Loss | 4.6859 | [5 empty] | Loss | 1.699 | [5 empty] | Loss | 0.56539 | [5 empty] | Loss | 0 |  |  |  |  | Loss | 0 |  |  |  | Loss | 0 |  |  |  |  | Loss | 0 |  |  |  |  | Loss | 0
| Adj.Flowrate | 226.7438 | [5 empty] | Adj.Flowrate | 187.8386 | [5 empty] | Adj.Flowrate | 157.6511 | [5 empty] | Adj.Flowrate | 137.5941 | [5 empty] | Adj.Flowrate | 115.961 | [5 empty] | Adj.Flowrate | 100.2946 | [5 empty] | Adj.Flowrate | 84.06 |  |  |  |  | Adj.Flowrate | 68.42 |  |  |  | Adj.Flowrate | 59.44 |  |  |  |  | Adj.Flowrate | 51.62 |  |  |  |  | Adj.Flowrate | 43.8
| SWL Adjustment from D0 | 0 | [5 empty] | SWL Adjustment from D1 | -0.81751 | [5 empty] | SWL Adjustment from D2 | -1.5784 | [5 empty] | SWL Adjustment from D3 | -2.1694 | [5 empty] | SWL Adjustment from D4 | -2.9122 | [5 empty] | SWL Adjustment from D5 | -3.5426 | [5 empty] | SWL Adjustment from D6 | -4.3095 |  |  |  |  | SWL Adjustment from D7 | -5.2035 |  |  |  | SWL Adjustment from D8 | -5.8146 |  |  |  |  | SWL Adjustment from D9 | -6.4272 |  |  |  |  | SWL Adjustment from D10 | -7.1406
| SWL A | 14.907 | [5 empty] | SWL A | 14.907 | [5 empty] | SWL A | 14.907 | [5 empty] | SWL A | 14.907 | [5 empty] | SWL A | 14.907 | [5 empty] | SWL A | 14.907 | [5 empty] | SWL A | 14.907 |  |  |  |  | SWL A | 14.907 |  |  |  | SWL A | 14.907 |  |  |  |  | SWL A | 14.907 |  |  |  |  | SWL A | 14.907
| SWL B | -5.8524 | [5 empty] | SWL B | -6.6699 | [5 empty] | SWL B | -7.4308 | [5 empty] | SWL B | -8.0218 | [5 empty] | SWL B | -8.7646 | [5 empty] | SWL B | -9.395 | [5 empty] | SWL B | -10.1619 |  |  |  |  | SWL B | -11.0559 |  |  |  | SWL B | -11.667 |  |  |  |  | SWL B | -12.2796 |  |  |  |  | SWL B | -12.993
| SWL @ 6.2 Pa | 21.3616 | fixed vane assumption |  |  |  |  | SWL @ 8.8 Pa | 25.7669 | fixed vane assumption |  |  |  |  | SWL @ 12.4 Pa | 30.1246 | fixed vane assumption |  |  |  |  | SWL @ 16.3 Pa | 33.6058 | fixed vane assumption |  |  |  |  | SWL @ 23.1 Pa | 38.0723 | fixed vane assumption |  |  |  |  | SWL @ 29.5 Pa | 41.0514 | fixed vane assumption |  |  |  |  | SWL @ 42.5 Pa | 45.7167 | fixed vane assumption |  |  |  | SWL @ 64.1 Pa | 50.9603 | fixed vane assumption |  |  | SWL @ 84.9 Pa | 54.544 | fixed vane assumption |  |  |  | SWL @ 112.6 Pa | 58.1369 | fixed vane assumption |  |  |  | SWL @ 156.4 Pa | 62.3212 | fixed vane assumption
| HSC-VS Face SWL | 21.3849 | [5 empty] | HSC-VS Face SWL | 21.3849 | [5 empty] | HSC-VS Face SWL | 21.3849 | [5 empty] | HSC-VS Face SWL | 21.3849 | [5 empty] | HSC-VS Face SWL | 21.3849 | [5 empty] | HSC-VS Face SWL | 21.3849 | [5 empty] | HSC-VS Face SWL | 21.3849 |  |  |  |  | HSC-VS Face SWL | 21.3849 |  |  |  | HSC-VS Face SWL | 21.3849 |  |  |  |  | HSC-VS Face SWL | 21.3849 |  |  |  |  | HSC-VS Face SWL | 21.3849
| Basket Only (P) | [6 empty] | Basket Only (P) | [6 empty] | Basket Only (P) | [6 empty] | Basket Only (P) | [6 empty] | Basket Only (P) | [6 empty] | Basket Only (P) | [6 empty] | Basket Only (P) | [5 empty] | Basket Only (P) |  |  |  |  | Basket Only (P) | [5 empty] | Basket Only (P) | [5 empty] | Basket Only (P)
| LN(P) | SWL @ 27.0% | [5 empty] | LN(P) | SWL @ 34.0% | [5 empty] | LN(P) | SWL @ 44.0% | [5 empty] | LN(P) | SWL @ 55.0% | [5 empty] | LN(P) | SWL @ 67.0% | [5 empty] | LN(P) | SWL @ 78.0% | [5 empty] | LN(P) | SWL @ 104.0% |  |  |  |  | LN(P) | SWL @ 163.0% |  |  |  | LN(P) | SWL @ 238.0% |  |  |  |  | LN(P) | SWL @ 751.0% |  |  |  |  | LN(P) | SWL @ 1033.0%
| 4.0943 | 45.176 | [5 empty] | 4.0943 | 45.4216 | [5 empty] | 4.0943 | 45.7753 | [5 empty] | 4.0943 | 46.1615 | [5 empty] | 4.0943 | 46.5698 | [5 empty] | 4.0943 | 46.9232 | [5 empty] | 4.0943 | 47.6301 |  |  |  |  | 4.0943 | 48.0625 |  |  |  | 4.0943 | 44.5876 |  |  |  |  | 4.0943 | -303.4756 |  |  |  |  | 4.0943 | -939.2069
| 2.9957 | 32.5023 | [5 empty] | 2.9957 | 32.7952 | [5 empty] | 2.9957 | 32.5204 | [5 empty] | 2.9957 | 31.6628 | [5 empty] | 2.9957 | 30.6088 | [5 empty] | 2.9957 | 30.0487 | [5 empty] | 2.9957 | 33.0886 |  |  |  |  | 2.9957 | 91.5373 |  |  |  | 2.9957 | 365.3403 |  |  |  |  | 2.9957 | 19901.5954 |  |  |  |  | 2.9957 | 55437.1628
| 40 | 11.5361 | -2.0567 |  |  |  |  | 40 | 11.493 | -1.6347 |  |  |  |  | 40 | 12.0652 | -3.6236 |  |  |  |  | 40 | 13.1972 | -7.8726 |  |  |  |  | 40 | 14.5283 | -12.9139 |  |  |  |  | 40 | 15.3598 | -15.9651 |  |  |  |  | 40 | 13.2362 | -6.5636 |  |  |  | 40 | -39.5725 | 210.0859 |  |  | 40 | -291.9617 | 1239.9796 |  |  |  | 40 | -18391.4482 | 74997.4505 |  |  |  | 40 | -51315.9831 | 209166.1097
| Adjustments | 41.7985 | [5 empty] | Adjustments | 41.2441 | [5 empty] | Adjustments | 40.6049 | [5 empty] | Adjustments | 39.9411 | [5 empty] | Adjustments | 39.0668 | [5 empty] | Adjustments | 38.4527 | [5 empty] | Adjustments | 39.2538 |  |  |  |  | Adjustments | 60.2043 |  |  |  | Adjustments | 158.4533 |  |  |  |  | Adjustments | 7148.4878 |  |  |  |  | Adjustments | 19861.7932
| Basket + Face Addition | 41.8378 | [5 empty] | Basket + Face Addition | 41.2887 | [5 empty] | Basket + Face Addition | 40.6566 | [5 empty] | Basket + Face Addition | 40.0012 | [5 empty] | Basket + Face Addition | 39.1403 | [5 empty] | Basket + Face Addition | 38.5372 | [5 empty] | Basket + Face Addition | 39.3241 |  |  |  |  | Basket + Face Addition | 60.2048 |  |  |  | Basket + Face Addition | 158.4533 |  |  |  |  | Basket + Face Addition | #NUM! |  |  |  |  | Basket + Face Addition | #NUM!
| SWL | 41.8378 | dB(A) |  |  |  |  | SWL | 41.2887 | dB(A) |  |  |  |  | SWL | 40.6566 | dB(A) |  |  |  |  | SWL | 40.0012 | dB(A) |  |  |  |  | SWL | 39.1403 | dB(A) |  |  |  |  | SWL | 38.5372 | dB(A) |  |  |  |  | SWL | 39.3241 | dB(A) |  |  |  | SWL | 60.2048 | dB(A) |  |  | SWL | 158.4533 | dB(A) |  |  |  | SWL | #NUM! | dB(A) |  |  |  | SWL | #NUM! | dB(A)
| SPL | 26.8378 | NC |  |  |  |  | SPL | 26.2887 | [5 empty] | SPL | 25.6566 | [5 empty] | SPL | 25.0012 | [5 empty] | SPL | 24.1403 | [5 empty] | SPL | 23.5372 | [5 empty] | SPL | 24.3241 |  |  |  |  | SPL | 45.2048 |  |  |  | SPL | 143.4533 |  |  |  |  | SPL | #NUM! |  |  |  |  | SPL | #NUM!
| SWL at 100% Fully Open |  | dB(A)
| SWL at TD @ Design P |  | dB(A)
| Acoustic Pressure Factor??? |  | factor that we expect the pressure to increase by when turned down
| SWL at TD @ Pres*Factor |  | dB(A)
| Hmin | [6 empty] | Hmin | [6 empty] | Hmin | [6 empty] | Hmin | [6 empty] | Hmin | [6 empty] | Hmin | [6 empty] | Hmin | [5 empty] | Hmin
| Factor | 4.417 | [5 empty] | Factor | 4.417 | [5 empty] | Factor | 4.417 | [5 empty] | Factor | 4.417 | [5 empty] | Factor | 4.417 | [5 empty] | Factor | 4.417 | [5 empty] | Factor | 4.417 |  |  |  |  | Factor | 4.417 |  |  |  | Factor | 4.417 |  |  |  |  | Factor | 4.417 |  |  |  |  | Factor | 4.417
| H_min_90 | 2.2471 | [5 empty] | H_min_90 | 2.2471 | [5 empty] | H_min_90 | 2.2471 | [5 empty] | H_min_90 | 2.2471 | [5 empty] | H_min_90 | 2.2471 | [5 empty] | H_min_90 | 2.2471 | [5 empty] | H_min_90 | 2.2471 |  |  |  |  | H_min_90 | 2.3471 |  |  |  | H_min | 2.3471 |  |  | 0.0333 | 2.2 | H_min | 2.3471 |  |  | 0.0333 | 2.2 | H_min | 2.3471 |  |  | 0.0333 | 2.2
| ADPI | [6 empty] | ADPI | [40 empty] | ADPI |  |  |  |  | ADPI | [5 empty] | ADPI | [5 empty] | ADPI
| H_min | 95% | 2.3471 |  |  |  |  | H_min | 95% | 2.3471 |  |  |  |  | H_min | 95% | 2.3471 |  |  |  |  | H_min | 95% | 2.3471 |  |  |  |  | H_min | 95% | 2.3471 |  |  |  |  | H_min | 95% | 2.3471 |  |  |  |  | H_min | 95% | 2.3471 |  |  |  | H_min | 95% | 2.4471 |  |  | H_min | 95% | 2.4471 |  |  |  | H_min | 95% | 2.4471 |  |  |  | H_min | 95% | 2.4471
|  | 90% | 2.2471 | [5 empty] | 90% | 2.2471 | [5 empty] | 90% | 2.2471 | [5 empty] | 90% | 2.2471 | [5 empty] | 90% | 2.2471 | [5 empty] | 90% | 2.2471 | [5 empty] | 90% | 2.2471 |  |  |  |  | 90% | 2.3471 |  |  |  | 90% | 2.3471 |  |  |  |  | 90% | 2.3471 |  |  |  |  | 90% | 2.3471
|  | 85% | 2.1971 | [5 empty] | 85% | 2.1971 | [5 empty] | 85% | 2.1971 | [5 empty] | 85% | 2.1971 | [5 empty] | 85% | 2.1971 | [5 empty] | 85% | 2.1971 | [5 empty] | 85% | 2.1971 |  |  |  |  | 85% | 2.2971 |  |  |  | 85% | 2.2971 |  |  |  |  | 85% | 2.2971 |  |  |  |  | 85% | 2.2971
|  | 80% | 2.1471 | [5 empty] | 80% | 2.1471 | [5 empty] | 80% | 2.1471 | [5 empty] | 80% | 2.1471 | [5 empty] | 80% | 2.1471 | [5 empty] | 80% | 2.1471 | [5 empty] | 80% | 2.1471 |  |  |  |  | 80% | 2.2471 |  |  |  | 80% | 2.2471 |  |  |  |  | 80% | 2.2471 |  |  |  |  | 80% | 2.2471
|  | 70% | 2.0471 | [5 empty] | 70% | 2.0471 | [5 empty] | 70% | 2.0471 | [5 empty] | 70% | 2.0471 | [5 empty] | 70% | 2.0471 | [5 empty] | 70% | 2.0471 | [5 empty] | 70% | 2.0471 |  |  |  |  | 70% | 2.1471 |  |  |  | 70% | 2.1471 |  |  |  |  | 70% | 2.1471 |  |  |  |  | 70% | 2.1471
| Hmin | 2.2471 | 2.2471 |  |  |  |  | Hmin | 2.2471 | 2.2471 |  |  |  |  | Hmin | 2.2471 | 2.2471 |  |  |  |  | Hmin | 2.2471 | 2.2471 |  |  |  |  | Hmin | 2.2471 | 2.2471 |  |  |  |  | Hmin | 2.2471 | 2.2471 |  |  |  |  | Hmin | 2.2471 | 2.2471 |  |  |  | Hmin | 2.3471 | 2.3471 |  |  | Hmin | 2.3471 | 2.3471 |  |  |  | Hmin | 2.3471 | 2.3471 |  |  |  | Hmin | 2.3471 | 2.3471
| Distance Selection | [6 empty] | Distance Selection | [6 empty] | Distance Selection | [6 empty] | Distance Selection | [6 empty] | Distance Selection | [6 empty] | Distance Selection | [6 empty] | Distance Selection | [5 empty] | Distance Selection |  |  |  |  | Distance Selection | [5 empty] | Distance Selection | [5 empty] | Distance Selection
| Vmax | 219.8566 | [5 empty] | Vmax | 184.5269 | [5 empty] | Vmax | 155.4173 | [5 empty] | Vmax | 135.5755 | [5 empty] | Vmax | 113.8405 | [5 empty] | Vmax | 100.86 | [5 empty] | Vmax | 84.06 |  |  |  |  | Vmax | 68.42 |  |  |  | Vmax | 59.44 |  |  |  |  | Vmax | 51.62 |  |  |  |  | Vmax | 43.8
| Vmin | 65.957 | [5 empty] | Vmin | 55.3581 | [5 empty] | Vmin | 46.6252 | [5 empty] | Vmin | 40.6726 | [5 empty] | Vmin | 34.1521 | [5 empty] | Vmin | 30.258 | [5 empty] | Vmin | 25.218 |  |  |  |  | Vmin | 20.526 |  |  |  | Vmin | 17.832 |  |  |  |  | Vmin | 15.486 |  |  |  |  | Vmin | 13.14
| Coverage Min | [6 empty] | R min | [6 empty] | R min | [6 empty] | R min | [6 empty] | R min | [6 empty] | R min | [6 empty] | R min | [5 empty] | R min |  |  |  |  | R min | [5 empty] | R min | [5 empty] | R min
| v'@ V | 19.086 | [5 empty] | v'@ V | 18.5883 | [5 empty] | v'@ V | 18.0083 | [5 empty] | v'@ V | 17.4702 | [5 empty] | v'@ V | 16.6655 | [5 empty] | v'@ V | 16.0195 | [5 empty] | v'@ V | 14.8872 |  |  |  |  | v'@ V | 13.3333 |  |  |  | v'@ V | 12.0715 |  |  |  |  | v'@ V | 10.6152 |  |  |  |  | v'@ V | 8.6387
| R min | 1.1445 | 2.289 |  |  |  |  | R min | 1.1597 | [5 empty] | R min | 1.1782 | [5 empty] | R min | 1.1962 | [5 empty] | R min | 1.2248 | [5 empty] | R min | 1.2492 | [5 empty] | R min | 1.2959 |  |  |  |  | R min | 1.3693 |  |  |  | R min | 1.4391 |  |  |  |  | R min | 1.5346 |  |  |  |  | R min | 1.7012
| Coverage Min | 2.289 | [5 empty] | Coverage Min | 2.3194 | [5 empty] | Coverage Min | 2.3565 | [5 empty] | Coverage Min | 2.3925 | [5 empty] | Coverage Min | 2.4496 | [5 empty] | Coverage Min | 2.4985 | [5 empty] | Coverage Min | 2.5918 |  |  |  |  | Coverage Min | 2.7386 |  |  |  | Coverage Min | 2.8782 |  |  |  |  | Coverage Min | 3.0693 |  |  |  |  | Coverage Min | 3.4023
| Coverage max NEW | [6 empty] | Coverage max NEW | [6 empty] | Coverage max NEW | [6 empty] | Coverage max NEW | [6 empty] | Coverage max NEW | [6 empty] | Coverage max NEW | [6 empty] | Coverage max NEW | [5 empty] | Coverage max NEW |  |  |  |  | Coverage max NEW | [5 empty] | Coverage max NEW | [5 empty] | Coverage max NEW
| f_Pressure | 0.98794 | [5 empty] | f_Pressure | 0.96189 | [5 empty] | f_Pressure | 0.9258 | [5 empty] | f_Pressure | 0.88679 | [5 empty] | f_Pressure | 0.81851 | [5 empty] | f_Pressure | 0.75509 | [5 empty] | f_Pressure | 0.62544 |  |  |  |  | f_Pressure | 0.40915 |  |  |  | f_Pressure | 0.20089 |  |  |  |  | f_Pressure | -0.075862 |  |  |  |  | f_Pressure | -0.51377
| H Factor | 4.7664 | [5 empty] | H Factor | 4.8037 | [5 empty] | H Factor | 4.8472 | [5 empty] | H Factor | 4.8875 | [5 empty] | H Factor | 4.9479 | [5 empty] | H Factor | 4.9963 | [5 empty] | H Factor | 5.0813 |  |  |  |  | H Factor | 5.1978 |  |  |  | H Factor | 5.2924 |  |  |  |  | H Factor | 5.4017 |  |  |  |  | H Factor | 5.5499
| Centre Zone | [6 empty] | Centre Zone | [6 empty] | Centre Zone | [6 empty] | Centre Zone | [6 empty] | Centre Zone | [6 empty] | Centre Zone | [6 empty] | Centre Zone | [5 empty] | Centre Zone |  |  |  |  | Centre Zone | [5 empty] | Centre Zone | [5 empty] | Centre Zone
| v" Centre Zone | 0.42721 | [5 empty] | v" Centre Zone | 0.41595 | [5 empty] | v" Centre Zone | 0.40034 | [5 empty] | v" Centre Zone | 0.38347 | [5 empty] | v" Centre Zone | 0.35395 | [5 empty] | v" Centre Zone | 0.32652 | [5 empty] | v" Centre Zone | 0.27046 |  |  |  |  | v" Centre Zone | 0.17693 |  |  |  | v" Centre Zone | 0.086871 |  |  |  |  | v" Centre Zone | -0.032805 |  |  |  |  | v" Centre Zone | -0.22217
| v" Centre Zone 0.35 l/s/m2 | 0.42721 | [5 empty] | v" Centre Zone 0.35 l/s/m3 | 0.41595 | [5 empty] | v" Centre Zone 0.35 l/s/m4 | 0.40034 | [5 empty] | v" Centre Zone 0.35 l/s/m5 | 0.38347 | [5 empty] | v" Centre Zone 0.35 l/s/m6 | 0.35395 | [5 empty] | v" Centre Zone 0.35 l/s/m7 | 0.35 | [5 empty] | v" Centre Zone 0.35 l/s/m8 | 0.35 |  |  |  |  | v" Centre Zone 0.35 l/s/m9 | 0.35 |  |  |  | v" Centre Zone 0.35 l/s/m10 | 0.35 |  |  |  |  | v" Centre Zone 0.35 l/s/m11 | 0.35 |  |  |  |  | v" Centre Zone 0.35 l/s/m12 | 0.35
| R max from v" | 4.19 | 8.3799 |  |  |  |  | R max from v" | 4.2463 | 8.4926 |  |  |  |  | R max from v" | 4.3283 | 8.6566 |  |  |  |  | R max from v" | 4.4225 | 8.8449 |  |  |  |  | R max from v" | 4.6032 | 9.2064 |  |  |  |  | R max from v" | 4.6291 | 9.2582 |  |  |  |  | R max from v" | 4.6291 | 9.2582 |  |  |  | R max from v" | 4.6291 | 9.2582 |  |  | R max from v" | 4.6291 | 9.2582 |  |  |  | R max from v" | 4.6291 | 9.2582 |  |  |  | R max from v" | 4.6291 | 9.2582
| R_max_roomheight | 6.4346 | 12.8692 |  |  |  |  | R_max_roomheight | 6.485 | 12.9699 |  |  |  |  | R_max_roomheight | 6.5437 | 13.0874 |  |  |  |  | R_max_roomheight | 6.5982 | 13.1964 |  |  |  |  | R_max_roomheight | 6.6797 | 13.3593 |  |  |  |  | R_max_roomheight | 6.7451 | 13.4901 |  |  |  |  | R_max_roomheight | 6.8597 | 13.7194 |  |  |  | R_max_roomheight | 7.017 | 14.0341 |  |  | R_max_roomheight | 7.1448 | 14.2896 |  |  |  | R_max_roomheight | 7.2923 | 14.5845 |  |  |  | R_max_roomheight | 7.4924 | 14.9847
| select | 4.19 | [5 empty] | select | 4.2463 | [5 empty] | select | 4.3283 | [5 empty] | select | 4.4225 | [5 empty] | select | 4.6032 | [5 empty] | select | 4.6291 | [5 empty] | select | 4.6291 |  |  |  |  | select | 4.6291 |  |  |  | select | 4.6291 |  |  |  |  | select | 4.6291 |  |  |  |  | select | 4.6291
| Coverage | 8.3799 | [5 empty] | Coverage | 8.4926 | [5 empty] | Coverage | 8.6566 | [5 empty] | Coverage | 8.8449 | [5 empty] | Coverage | 9.2064 | [5 empty] | Coverage | 9.2582 | [5 empty] | Coverage | 9.2582 |  |  |  |  | Coverage | 9.2582 |  |  |  | Coverage | 9.2582 |  |  |  |  | Coverage | 9.2582 |  |  |  |  | Coverage | 9.2582
| Perimeter Zone Cmax | [6 empty] | Perimeter Zone Cmax | [6 empty] | Perimeter Zone Cmax | [6 empty] | Perimeter Zone Cmax | [6 empty] | Perimeter Zone Cmax | [6 empty] | Perimeter Zone Cmax | [6 empty] | Perimeter Zone Cmax | [5 empty] | Perimeter Zone Cmax |  |  |  |  | Perimeter Zone Cmax | [5 empty] | Perimeter Zone Cmax | [5 empty] | Perimeter Zone Cmax
| v" Perimeter Zone | 0.52855 | [5 empty] | v" Perimeter Zone | 0.51461 | [5 empty] | v" Perimeter Zone | 0.4953 | [5 empty] | v" Perimeter Zone | 0.47443 | [5 empty] | v" Perimeter Zone | 0.4379 | [5 empty] | v" Perimeter Zone | 0.40398 | [5 empty] | v" Perimeter Zone | 0.33461 |  |  |  |  | v" Perimeter Zone | 0.2189 |  |  |  | v" Perimeter Zone | 0.10748 |  |  |  |  | v" Perimeter Zone | -0.040586 |  |  |  |  | v" Perimeter Zone | -0.27487
| v" Perimeter Zone 0.35 L/s/m2 | 0.52855 | [5 empty] | v" Perimeter Zone 0.35 L/s/m3 | 0.51461 | [5 empty] | v" Perimeter Zone 0.35 L/s/m4 | 0.4953 | [5 empty] | v" Perimeter Zone 0.35 L/s/m5 | 0.47443 | [5 empty] | v" Perimeter Zone 0.35 L/s/m6 | 0.4379 | [5 empty] | v" Perimeter Zone 0.35 L/s/m7 | 0.40398 | [5 empty] | v" Perimeter Zone 0.35 L/s/m8 | 0.35 |  |  |  |  | v" Perimeter Zone 0.35 L/s/m9 | 0.35 |  |  |  | v" Perimeter Zone 0.35 L/s/m10 | 0.35 |  |  |  |  | v" Perimeter Zone 0.35 L/s/m11 | 0.35 |  |  |  |  | v" Perimeter Zone 0.35 L/s/m12 | 0.35
| R max from v" | 3.7669 | 7.5339 |  |  |  |  | R max from v" | 3.8176 | 7.6352 |  |  |  |  | R max from v" | 3.8913 | 7.7826 |  |  |  |  | R max from v" | 3.976 | 7.952 |  |  |  |  | R max from v" | 4.1385 | 8.277 |  |  |  |  | R max from v" | 4.3088 | 8.6175 |  |  |  |  | R max from v" | 4.6291 | 9.2582 |  |  |  | R max from v" | 4.6291 | 9.2582 |  |  | R max from v" | 4.6291 | 9.2582 |  |  |  | R max from v" | 4.6291 | 9.2582 |  |  |  | R max from v" | 4.6291 | 9.2582
| R_max_roomheight | 6.4346 | 12.8692 |  |  |  |  | R_max_roomheight | 6.485 | 12.9699 |  |  |  |  | R_max_roomheight | 6.5437 | 13.0874 |  |  |  |  | R_max_roomheight | 6.5982 | 13.1964 |  |  |  |  | R_max_roomheight | 6.6797 | 13.3593 |  |  |  |  | R_max_roomheight | 6.7451 | 13.4901 |  |  |  |  | R_max_roomheight | 6.8597 | 13.7194 |  |  |  | R_max_roomheight | 7.017 | 14.0341 |  |  | R_max_roomheight | 7.1448 | 14.2896 |  |  |  | R_max_roomheight | 7.2923 | 14.5845 |  |  |  | R_max_roomheight | 7.4924 | 14.9847
| select | 3.7669 | [5 empty] | select | 3.8176 | [5 empty] | select | 3.8913 | [5 empty] | select | 3.976 | [5 empty] | select | 4.1385 | [5 empty] | select | 4.3088 | [5 empty] | select | 4.6291 |  |  |  |  | select | 4.6291 |  |  |  | select | 4.6291 |  |  |  |  | select | 4.6291 |  |  |  |  | select | 4.6291
| Coverage | 7.5339 | [5 empty] | Coverage | 7.6352 | [5 empty] | Coverage | 7.7826 | [5 empty] | Coverage | 7.952 | [5 empty] | Coverage | 8.277 | [5 empty] | Coverage | 8.6175 | [5 empty] | Coverage | 9.2582 |  |  |  |  | Coverage | 9.2582 |  |  |  | Coverage | 9.2582 |  |  |  |  | Coverage | 9.2582 |  |  |  |  | Coverage | 9.2582
| Heating | [6 empty] | Heating | [6 empty] | Heating | [6 empty] | Heating | [6 empty] | Heating | [6 empty] | Heating | [6 empty] | Heating | [5 empty] | Heating |  |  |  |  | Heating | [5 empty] | Heating | [5 empty] | Heating
| Ax^2 | -6.8984e-06 | [5 empty] | Ax^2 | -3.7349e-05 | [5 empty] | Ax^2 | -6.593e-05 | [5 empty] | Ax^2 | -8.7367e-05 | [5 empty] | Ax^2 | -0.00011263 | [5 empty] | Ax^2 | -0.00013217 | [5 empty] | Ax^2 | -0.00015359 |  |  |  |  | Ax^2 | -0.00017586 |  |  |  | Ax^2 | -0.00018872 |  |  |  |  | Ax^2 | -0.00020067 |  |  |  |  | Ax^2 | -0.00021294
| Bx | 0.06227 | [5 empty] | Bx | 0.071405 | [5 empty] | Bx | 0.079979 | [5 empty] | Bx | 0.08641 | [5 empty] | Bx | 0.093988 | [5 empty] | Bx | 0.09985 | [5 empty] | Bx | 0.10628 |  |  |  |  | Bx | 0.11296 |  |  |  | Bx | 0.11682 |  |  |  |  | Bx | 0.1204 |  |  |  |  | Bx | 0.12408
| C | -1.1828 | [5 empty] | C | -1.1846 | [5 empty] | C | -1.1484 | [5 empty] | C | -1.107 | [5 empty] | C | -1.0472 | [5 empty] | C | -0.99464 | [5 empty] | C | -0.9319 |  |  |  |  | C | -0.86194 |  |  |  | C | -0.81966 |  |  |  |  | C | -0.77923 |  |  |  |  | C | -0.73672
| heatingX | 4.9752 | [5 empty] | heatingX | 5.5824 | [5 empty] | heatingX | 6.1902 | [5 empty] | heatingX | 6.6604 | [5 empty] | heatingX | 7.2253 | [5 empty] | heatingX | 7.6687 | [5 empty] | heatingX | 8.1599 |  |  |  |  | heatingX | 8.6753 |  |  |  | heatingX | 8.9747 |  |  |  |  | heatingX | 9.2543 |  |  |  |  | heatingX | 9.5421
| heatingSlope | 0.67328 | [5 empty] | heatingSlope | 0.67328 | [5 empty] | heatingSlope | 0.67328 | [5 empty] | heatingSlope | 0.67328 | [5 empty] | heatingSlope | 0.67328 | [5 empty] | heatingSlope | 0.67328 | [5 empty] | heatingSlope | 0.67328 |  |  |  |  | heatingSlope | 0.67328 |  |  |  | heatingSlope | 0.67328 |  |  |  |  | heatingSlope | 0.67328 |  |  |  |  | heatingSlope | 0.67328
| heatingY | 3.3497 | [5 empty] | heatingY | 3.7585 | [5 empty] | heatingY | 4.1678 | [5 empty] | heatingY | 4.4843 | [5 empty] | heatingY | 4.8647 | [5 empty] | heatingY | 5.1632 | [5 empty] | heatingY | 5.4939 |  |  |  |  | heatingY | 5.841 |  |  |  | heatingY | 6.0426 |  |  |  |  | heatingY | 6.2307 |  |  |  |  | heatingY | 6.4246
| dT_10L/s | 7.4363 | [5 empty] | dT_10L/s | 8.3439 | [5 empty] | dT_10L/s | 9.2525 | [5 empty] | dT_10L/s | 9.9552 | [5 empty] | dT_10L/s | 10.7996 | [5 empty] | dT_10L/s | 11.4623 | [5 empty] | dT_10L/s | 12.1965 |  |  |  |  | dT_10L/s | 12.9669 |  |  |  | dT_10L/s | 13.4145 |  |  |  |  | dT_10L/s | 13.8322 |  |  |  |  | dT_10L/s | 14.2625
| specVfactor | 0.74835 | [5 empty] | specVfactor | 0.74835 | [5 empty] | specVfactor | 0.74835 | [5 empty] | specVfactor | 0.74835 | [5 empty] | specVfactor | 0.74835 | [5 empty] | specVfactor | 0.74835 | [5 empty] | specVfactor | 0.74835 |  |  |  |  | specVfactor | 0.74835 |  |  |  | specVfactor | 0.74835 |  |  |  |  | specVfactor | 0.74835 |  |  |  |  | specVfactor | 0.74835
| dT_heating | 5.5649 | [5 empty] | dT_heating | 6.2442 | [5 empty] | dT_heating | 6.924 | [5 empty] | dT_heating | 7.4499 | [5 empty] | dT_heating | 8.0818 | [5 empty] | dT_heating | 8.5778 | [5 empty] | dT_heating | 9.1272 |  |  |  |  | dT_heating | 9.7037 |  |  |  | dT_heating | 10.0387 |  |  |  |  | dT_heating | 10.3513 |  |  |  |  | dT_heating | 10.6733
| dT_heating Centre | 8.3474 | [5 empty] | dT_heating Centre | 9.3662 | [5 empty] | dT_heating Centre | 10.3861 | [5 empty] | dT_heating Centre | 11.1749 | [5 empty] | dT_heating Centre | 12.1228 | [5 empty] | dT_heating Centre | 12.8667 | [5 empty] | dT_heating Centre | 13.6908 |  |  |  |  | dT_heating Centre | 14.5556 |  |  |  | dT_heating Centre | 15.058 |  |  |  |  | dT_heating Centre | 15.5269 |  |  |  |  | dT_heating Centre | 16.0099
| DR | [6 empty] | DR | [6 empty] | DR | [6 empty] | DR | [6 empty] | DR | [6 empty] | DR | [6 empty] | DR | [5 empty] | DR |  |  |  |  | DR | [5 empty] | DR | [5 empty] | DR
| velocity adjustment | [6 empty] | velocity adjustment | [6 empty] | velocity adjustment | [6 empty] | velocity adjustment | [6 empty] | velocity adjustment | [6 empty] | velocity adjustment | [6 empty] | velocity adjustment | [5 empty] | velocity adjustment |  |  |  |  | velocity adjustment | [5 empty] | velocity adjustment | [5 empty] | velocity adjustment
| v'' correction factor | 0.56463 | [5 empty] | v'' correction factor | 0.47443 | [5 empty] | v'' correction factor | 0.36931 | [5 empty] | v'' correction factor | 0.27178 | [5 empty] | v'' correction factor | 0.12592 | [5 empty] | v'' correction factor | 0.0088312 | [5 empty] | v'' correction factor | -0.1964 |  |  |  |  | v'' correction factor | -0.47805 |  |  |  | v'' correction factor | -0.70674 |  |  |  |  | v'' correction factor | -0.97071 |  |  |  |  | v'' correction factor | -1.3289
| v'' (adjusted) | 2.3354 | [5 empty] | v'' (adjusted) | 2.4256 | [5 empty] | v'' (adjusted) | 2.5307 | [5 empty] | v'' (adjusted) | 2.6282 | [5 empty] | v'' (adjusted) | 2.7741 | [5 empty] | v'' (adjusted) | 2.8912 | [5 empty] | v'' (adjusted) | 3.0964 |  |  |  |  | v'' (adjusted) | 3.378 |  |  |  | v'' (adjusted) | 3.6067 |  |  |  |  | v'' (adjusted) | 3.8707 |  |  |  |  | v'' (adjusted) | 4.2289
| Q'' (adjusted) | 28.0245 | [5 empty] | Q'' (adjusted) | 29.1068 | [5 empty] | Q'' (adjusted) | 30.3683 | [5 empty] | Q'' (adjusted) | 31.5387 | [5 empty] | Q'' (adjusted) | 33.289 | [5 empty] | Q'' (adjusted) | 34.694 | [5 empty] | Q'' (adjusted) | 37.1568 |  |  |  |  | Q'' (adjusted) | 40.5365 |  |  |  | Q'' (adjusted) | 43.2809 |  |  |  |  | Q'' (adjusted) | 46.4485 |  |  |  |  | Q'' (adjusted) | 50.7472
| 2.7 | 0.02455 | 0.4405 | 0.10658 |  |  |  | 2.7 | 0.0246 | 0.441 | 0.10878 |  |  |  | 2.7 | 0.0246 | 0.441 | 0.11084 |  |  |  | 2.7 | 0.0246 | 0.441 | 0.1127 |  |  |  | 2.7 | 0.0246 | 0.441 | 0.11542 |  |  |  | 2.7 | 0.0246 | 0.441 | 0.11754 |  |  |  | 2.7 | 0.0246 | 0.441 | 0.12115 |  |  | 2.7 | 0.02455 | 0.4405 | 0.1254 |  | 2.7 | 0.02455 | 0.4405 | 0.12907 |  |  | 2.7 | 0.02455 | 0.4405 | 0.13315 |  |  | 2.7 | 0.02455 | 0.4405 | 0.13845
| 4 | 0.0251 | 0.4458 | 0.11091 |  |  |  | 4 | 0.0251 | 0.446 | 0.11288 |  |  |  | 4 | 0.0251 | 0.446 | 0.11504 |  |  |  | 4 | 0.0251 | 0.446 | 0.11699 |  |  |  | 4 | 0.0251 | 0.446 | 0.11984 |  |  |  | 4 | 0.0251 | 0.446 | 0.12208 |  |  |  | 4 | 0.0251 | 0.446 | 0.12587 |  |  | 4 | 0.0251 | 0.4458 | 0.13075 |  | 4 | 0.0251 | 0.4458 | 0.13463 |  |  | 4 | 0.0251 | 0.4458 | 0.13893 |  |  | 4 | 0.0251 | 0.4458 | 0.14453
| 10 | 0.02797 | 0.4391 | 0.12087 |  |  |  | 10 | 0.028 | 0.439 | 0.12298 |  |  |  | 10 | 0.028 | 0.439 | 0.1253 |  |  |  | 10 | 0.028 | 0.439 | 0.12739 |  |  |  | 10 | 0.028 | 0.439 | 0.13045 |  |  |  | 10 | 0.028 | 0.439 | 0.13284 |  |  |  | 10 | 0.028 | 0.439 | 0.1369 |  |  | 10 | 0.02797 | 0.4391 | 0.14213 |  | 10 | 0.02797 | 0.4391 | 0.14628 |  |  | 10 | 0.02797 | 0.4391 | 0.15089 |  |  | 10 | 0.02797 | 0.4391 | 0.15687
| Room height | Ax | ^b |  |  |  |  | Room height | Ax | ^b |  |  |  |  | Room height | Ax | ^b |  |  |  |  | Room height | Ax | ^b |  |  |  |  | Room height | Ax | ^b |  |  |  |  | Room height | Ax | ^b |  |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b |  |  |  | Room height | Ax | ^b
| 2.7 | 0.097014 | 0.095644 | 0.10668 | m/s |  |  | 2.7 | 0.099121 | 0.093697 | 0.10879 | m/s |  |  | 2.7 | 0.10101 | 0.093587 | 0.11085 | m/s |  |  | 2.7 | 0.10273 | 0.093488 | 0.11273 | m/s |  |  | 2.7 | 0.10524 | 0.093347 | 0.11546 | m/s |  |  | 2.7 | 0.1072 | 0.093239 | 0.1176 | m/s |  |  | 2.7 | 0.11053 | 0.09306 | 0.12123 | m/s |  | 2.7 | 0.11434 | 0.094842 | 0.12564 | m/s | 2.7 | 0.11772 | 0.094699 | 0.12934 | m/s |  | 2.7 | 0.12149 | 0.094546 | 0.13345 | m/s |  | 2.7 | 0.12637 | 0.094353 | 0.13878
| Velocity | 0.10668 | [5 empty] | Velocity | 0.10879 | [5 empty] | Velocity | 0.11085 | [5 empty] | Velocity | 0.11273 | [5 empty] | Velocity | 0.11546 | [5 empty] | Velocity | 0.1176 | [5 empty] | Velocity | 0.12123 |  |  |  |  | Velocity | 0.12564 |  |  |  | Velocity | 0.12934 |  |  |  |  | Velocity | 0.13345 |  |  |  |  | Velocity | 0.13878
| Draught Rating | 8.757% | [5 empty] | Draught Rating | 9.017% | [5 empty] | Draught Rating | 9.271% | [5 empty] | Draught Rating | 9.502% | [5 empty] | Draught Rating | 9.839% | [5 empty] | Draught Rating | 10.1% | [5 empty] | Draught Rating | 10.55% |  |  |  |  | Draught Rating | 11.09% |  |  |  | Draught Rating | 11.55% |  |  |  |  | Draught Rating | 12.06% |  |  |  |  | Draught Rating | 12.73%
| PPD | 5.573% | [5 empty] | PPD | 5.661% | [5 empty] | PPD | 5.748% | [5 empty] | PPD | 5.827% | [5 empty] | PPD | 5.944% | [5 empty] | PPD | 6.036% | [5 empty] | PPD | 6.194% |  |  |  |  | PPD | 6.389% |  |  |  | PPD | 6.556% |  |  |  |  | PPD | 6.744% |  |  |  |  | PPD | 6.993%
| PPD class | A | [5 empty] | PPD class | A | [5 empty] | PPD class | A | [5 empty] | PPD class | A | [5 empty] | PPD class | A | [5 empty] | PPD class | B | [5 empty] | PPD class | B |  |  |  |  | PPD class | B |  |  |  | PPD class | B |  |  |  |  | PPD class | B |  |  |  |  | PPD class | B
| PMV | 0.13624 | [5 empty] | PMV | 0.14947 | [5 empty] | PMV | 0.16207 | [5 empty] | PMV | 0.17321 | [5 empty] | PMV | 0.18897 | [5 empty] | PMV | 0.20092 | [5 empty] | PMV | 0.22057 |  |  |  |  | PMV | 0.24335 |  |  |  | PMV | 0.26169 |  |  |  |  | PMV | 0.28129 |  |  |  |  | PMV | 0.30562
| PMV | 0.2 | [5 empty] | PMV | 0.2 | [5 empty] | PMV | 0.2 | [5 empty] | PMV | 0.2 | [5 empty] | PMV | 0.2 | [5 empty] | PMV | 0.2 | [5 empty] | PMV | 0.2 | [5 empty] | 0.2 |  |  |  |  | 0.3 | [5 empty] | 0.3 | [5 empty] | 0.3
| Box Details | [6 empty] | Box Details | [6 empty] | Box Details | [6 empty] | Box Details | [6 empty] | Box Details | [6 empty] | Box Details | [6 empty] | Box Details | [5 empty] | Box Details |  |  |  |  | Box Details | [5 empty] | Box Details | [5 empty] | Box Details
| Diffuser pressure design/required | 40 | [5 empty] | Diffuser pressure design/required | 40 | [5 empty] | Diffuser pressure design/required | 40 | [5 empty] | Diffuser pressure design/required | 40 | [5 empty] | Diffuser pressure design/required | 40 | [5 empty] | Diffuser pressure design/required | 40 | [5 empty] | Diffuser pressure design/required | 42.4563 |  |  |  |  | Diffuser pressure design/required | 64.0848 |  |  |  | Diffuser pressure design/required | 84.9109 |  |  |  |  | Diffuser pressure design/required | 112.5862 |  |  |  |  | Diffuser pressure design/required | 156.3771
| 350 Box | [6 empty] | 350 Box | [6 empty] | 350 Box | [6 empty] | 350 Box | [6 empty] | 350 Box | [6 empty] | 350 Box | [6 empty] | 350 Box | [5 empty] | 350 Box |  |  |  |  | 350 Box | [5 empty] | 350 Box | [5 empty] | 350 Box
| Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 |  |  |  |  | Nominal Spigot Diameter | 200 |  |  |  | Nominal Spigot Diameter | 200 |  |  |  |  | Nominal Spigot Diameter | 200 |  |  |  |  | Nominal Spigot Diameter | 200
| Velocity | 3.2152 | [5 empty] | Velocity | 3.2152 | [5 empty] | Velocity | 3.2152 | [5 empty] | Velocity | 3.2152 | [5 empty] | Velocity | 3.2152 | [5 empty] | Velocity | 3.2152 | [5 empty] | Velocity | 3.2152 |  |  |  |  | Velocity | 3.2152 |  |  |  | Velocity | 3.2152 |  |  |  |  | Velocity | 3.2152 |  |  |  |  | Velocity | 3.2152
| Pd | 6.2024 | [5 empty] | Pd | 6.2024 | [5 empty] | Pd | 6.2024 | [5 empty] | Pd | 6.2024 | [5 empty] | Pd | 6.2024 | [5 empty] | Pd | 6.2024 | [5 empty] | Pd | 6.2024 |  |  |  |  | Pd | 6.2024 |  |  |  | Pd | 6.2024 |  |  |  |  | Pd | 6.2024 |  |  |  |  | Pd | 6.2024
| Pdrop Perf | 4.5017 | [5 empty] | Pdrop Perf | 4.5017 | [5 empty] | Pdrop Perf | 4.5017 | [5 empty] | Pdrop Perf | 4.5017 | [5 empty] | Pdrop Perf | 4.5017 | [5 empty] | Pdrop Perf | 4.5017 | [5 empty] | Pdrop Perf | 4.5017 |  |  |  |  | Pdrop Perf | 4.5017 |  |  |  | Pdrop Perf | 4.5017 |  |  |  |  | Pdrop Perf | 4.5017 |  |  |  |  | Pdrop Perf | 4.5017
| Static Pressure (Inlet) Req | 44.5017 | [5 empty] | Static Pressure (Inlet) Req | 44.5017 | [5 empty] | Static Pressure (Inlet) Req | 44.5017 | [5 empty] | Static Pressure (Inlet) Req | 44.5017 | [5 empty] | Static Pressure (Inlet) Req | 44.5017 | [5 empty] | Static Pressure (Inlet) Req | 44.5017 | [5 empty] | Static Pressure (Inlet) Req | 46.958 |  |  |  |  | Static Pressure (Inlet) Req | 68.5865 |  |  |  | Static Pressure (Inlet) Req | 89.4126 |  |  |  |  | Static Pressure (Inlet) Req | 117.0879 |  |  |  |  | Static Pressure (Inlet) Req | 160.8787
| Total Pressure (Inlet) | 50.704 | [5 empty] | Total Pressure (Inlet) | 50.704 | [5 empty] | Total Pressure (Inlet) | 50.704 | [5 empty] | Total Pressure (Inlet) | 50.704 | [5 empty] | Total Pressure (Inlet) | 50.704 | [5 empty] | Total Pressure (Inlet) | 50.704 | [5 empty] | Total Pressure (Inlet) | 53.1604 |  |  |  |  | Total Pressure (Inlet) | 74.7889 |  |  |  | Total Pressure (Inlet) | 95.615 |  |  |  |  | Total Pressure (Inlet) | 123.2903 |  |  |  |  | Total Pressure (Inlet) | 167.0811
| SWL Adj | 41.8378 | [5 empty] | SWL Adj | 41.2887 | [5 empty] | SWL Adj | 40.6566 | [5 empty] | SWL Adj | 40.0012 | [5 empty] | SWL Adj | 39.1403 | [5 empty] | SWL Adj | 38.5372 | [5 empty] | SWL Adj | 39.3241 |  |  |  |  | SWL Adj | 60.2048 |  |  |  | SWL Adj | 158.4533 |  |  |  |  | SWL Adj | #NUM! |  |  |  |  | SWL Adj | #NUM!
| SPL Adj | 26.8378 | [5 empty] | SPL Adj | 26.2887 | [5 empty] | SPL Adj | 25.6566 | [5 empty] | SPL Adj | 25.0012 | [5 empty] | SPL Adj | 24.1403 | [5 empty] | SPL Adj | 23.5372 | [5 empty] | SPL Adj | 24.3241 |  |  |  |  | SPL Adj | 45.2048 |  |  |  | SPL Adj | 143.4533 |  |  |  |  | SPL Adj | #NUM! |  |  |  |  | SPL Adj | #NUM!
| 250mm Standard connection Box | [6 empty] | 250mm Standard connection Box | [6 empty] | 250mm Standard connection Box | [6 empty] | 250mm Standard connection Box | [6 empty] | 250mm Standard connection Box | [6 empty] | 250mm Standard connection Box | [6 empty] | 250mm Standard connection Box | [5 empty] | 250mm Standard connection Box |  |  |  |  | 250mm Standard connection Box | [5 empty] | 250mm Standard connection Box | [5 empty] | 250mm Standard connection Box
| Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 |  |  |  |  | Nominal Spigot Diameter | 200 |  |  |  | Nominal Spigot Diameter | 200 |  |  |  |  | Nominal Spigot Diameter | 200 |  |  |  |  | Nominal Spigot Diameter | 200
| Velocity | 3.3011 | [5 empty] | Velocity | 3.3011 | [5 empty] | Velocity | 3.3011 | [5 empty] | Velocity | 3.3011 | [5 empty] | Velocity | 3.3011 | [5 empty] | Velocity | 3.3011 | [5 empty] | Velocity | 3.3011 |  |  |  |  | Velocity | 3.3011 |  |  |  | Velocity | 3.3011 |  |  |  |  | Velocity | 3.3011 |  |  |  |  | Velocity | 3.3011
| Pd | 6.5383 | [5 empty] | Pd | 6.5383 | [5 empty] | Pd | 6.5383 | [5 empty] | Pd | 6.5383 | [5 empty] | Pd | 6.5383 | [5 empty] | Pd | 6.5383 | [5 empty] | Pd | 6.5383 |  |  |  |  | Pd | 6.5383 |  |  |  | Pd | 6.5383 |  |  |  |  | Pd | 6.5383 |  |  |  |  | Pd | 6.5383
| Pdrop Perf | 6.2454 | [5 empty] | Pdrop Perf | 6.2454 | [5 empty] | Pdrop Perf | 6.2454 | [5 empty] | Pdrop Perf | 6.2454 | [5 empty] | Pdrop Perf | 6.2454 | [5 empty] | Pdrop Perf | 6.2454 | [5 empty] | Pdrop Perf | 6.2454 |  |  |  |  | Pdrop Perf | 6.2454 |  |  |  | Pdrop Perf | 6.2454 |  |  |  |  | Pdrop Perf | 6.2454 |  |  |  |  | Pdrop Perf | 6.2454
| Static Pressure (Inlet) Req | 46.2454 | [5 empty] | Static Pressure (Inlet) Req | 46.2454 | [5 empty] | Static Pressure (Inlet) Req | 46.2454 | [5 empty] | Static Pressure (Inlet) Req | 46.2454 | [5 empty] | Static Pressure (Inlet) Req | 46.2454 | [5 empty] | Static Pressure (Inlet) Req | 46.2454 | [5 empty] | Static Pressure (Inlet) Req | 48.7017 |  |  |  |  | Static Pressure (Inlet) Req | 70.3302 |  |  |  | Static Pressure (Inlet) Req | 91.1563 |  |  |  |  | Static Pressure (Inlet) Req | 118.8316 |  |  |  |  | Static Pressure (Inlet) Req | 162.6224
| Total Pressure (Inlet) | 52.7837 | [5 empty] | Total Pressure (Inlet) | 52.7837 | [5 empty] | Total Pressure (Inlet) | 52.7837 | [5 empty] | Total Pressure (Inlet) | 52.7837 | [5 empty] | Total Pressure (Inlet) | 52.7837 | [5 empty] | Total Pressure (Inlet) | 52.7837 | [5 empty] | Total Pressure (Inlet) | 55.24 |  |  |  |  | Total Pressure (Inlet) | 76.8685 |  |  |  | Total Pressure (Inlet) | 97.6946 |  |  |  |  | Total Pressure (Inlet) | 125.3699 |  |  |  |  | Total Pressure (Inlet) | 169.1607
| SWL Adj | 43.2597 | [5 empty] | SWL Adj | 42.7106 | [5 empty] | SWL Adj | 42.0784 | [5 empty] | SWL Adj | 41.4231 | [5 empty] | SWL Adj | 40.5621 | [5 empty] | SWL Adj | 39.9591 | [5 empty] | SWL Adj | 40.746 |  |  |  |  | SWL Adj | 61.6267 |  |  |  | SWL Adj | 159.8752 |  |  |  |  | SWL Adj | #NUM! |  |  |  |  | SWL Adj | #NUM!
| SPL Adj | 28.2597 | [5 empty] | SPL Adj | 27.7106 | [5 empty] | SPL Adj | 27.0784 | [5 empty] | SPL Adj | 26.4231 | [5 empty] | SPL Adj | 25.5621 | [5 empty] | SPL Adj | 24.9591 | [5 empty] | SPL Adj | 25.746 |  |  |  |  | SPL Adj | 46.6267 |  |  |  | SPL Adj | 144.8752 |  |  |  |  | SPL Adj | #NUM! |  |  |  |  | SPL Adj | #NUM!
| 200mm Ultra-Low Profile Box | [6 empty] | 200mm Ultra-Low Profile Box | [6 empty] | 200mm Ultra-Low Profile Box | [6 empty] | 200mm Ultra-Low Profile Box | [6 empty] | 200mm Ultra-Low Profile Box | [6 empty] | 200mm Ultra-Low Profile Box | [6 empty] | 200mm Ultra-Low Profile Box | [5 empty] | 200mm Ultra-Low Profile Box |  |  |  |  | 200mm Ultra-Low Profile Box | [5 empty] | 200mm Ultra-Low Profile Box | [5 empty] | 200mm Ultra-Low Profile Box
| Nominal Spigot Diameter | 250 | [5 empty] | Nominal Spigot Diameter | 250 | [5 empty] | Nominal Spigot Diameter | 250 | [5 empty] | Nominal Spigot Diameter | 250 | [5 empty] | Nominal Spigot Diameter | 250 | [5 empty] | Nominal Spigot Diameter | 250 | [5 empty] | Nominal Spigot Diameter | 250 |  |  |  |  | Nominal Spigot Diameter | 250 |  |  |  | Nominal Spigot Diameter | 250 |  |  |  |  | Nominal Spigot Diameter | 250 |  |  |  |  | Nominal Spigot Diameter | 250
| Velocity | 3.0941 | [5 empty] | Velocity | 3.0941 | [5 empty] | Velocity | 3.0941 | [5 empty] | Velocity | 3.0941 | [5 empty] | Velocity | 3.0941 | [5 empty] | Velocity | 3.0941 | [5 empty] | Velocity | 3.0941 |  |  |  |  | Velocity | 3.0941 |  |  |  | Velocity | 3.0941 |  |  |  |  | Velocity | 3.0941 |  |  |  |  | Velocity | 3.0941
| Pd | 5.744 | [5 empty] | Pd | 5.744 | [5 empty] | Pd | 5.744 | [5 empty] | Pd | 5.744 | [5 empty] | Pd | 5.744 | [5 empty] | Pd | 5.744 | [5 empty] | Pd | 5.744 |  |  |  |  | Pd | 5.744 |  |  |  | Pd | 5.744 |  |  |  |  | Pd | 5.744 |  |  |  |  | Pd | 5.744
| Pdrop Perf | 7.5273 | [5 empty] | Pdrop Perf | 7.5273 | [5 empty] | Pdrop Perf | 7.5273 | [5 empty] | Pdrop Perf | 7.5273 | [5 empty] | Pdrop Perf | 7.5273 | [5 empty] | Pdrop Perf | 7.5273 | [5 empty] | Pdrop Perf | 7.5273 |  |  |  |  | Pdrop Perf | 7.5273 |  |  |  | Pdrop Perf | 7.5273 |  |  |  |  | Pdrop Perf | 7.5273 |  |  |  |  | Pdrop Perf | 7.5273
| Static Pressure (Inlet) Req | 57.5273 | [5 empty] | Static Pressure (Inlet) Req | 47.5273 | [5 empty] | Static Pressure (Inlet) Req | 47.5273 | [5 empty] | Static Pressure (Inlet) Req | 47.5273 | [5 empty] | Static Pressure (Inlet) Req | 47.5273 | [5 empty] | Static Pressure (Inlet) Req | 47.5273 | [5 empty] | Static Pressure (Inlet) Req | 49.9836 |  |  |  |  | Static Pressure (Inlet) Req | 71.6121 |  |  |  | Static Pressure (Inlet) Req | 92.4382 |  |  |  |  | Static Pressure (Inlet) Req | 120.1135 |  |  |  |  | Static Pressure (Inlet) Req | 163.9043
| Total Pressure (Inlet) | 63.2713 | [5 empty] | Total Pressure (Inlet) | 53.2713 | [5 empty] | Total Pressure (Inlet) | 53.2713 | [5 empty] | Total Pressure (Inlet) | 53.2713 | [5 empty] | Total Pressure (Inlet) | 53.2713 | [5 empty] | Total Pressure (Inlet) | 53.2713 | [5 empty] | Total Pressure (Inlet) | 55.7276 |  |  |  |  | Total Pressure (Inlet) | 77.3561 |  |  |  | Total Pressure (Inlet) | 98.1822 |  |  |  |  | Total Pressure (Inlet) | 125.8575 |  |  |  |  | Total Pressure (Inlet) | 169.6483
| SWL Adj | 47.0705 | [5 empty] | SWL Adj | 46.5214 | [5 empty] | SWL Adj | 45.8892 | [5 empty] | SWL Adj | 45.2339 | [5 empty] | SWL Adj | 44.3729 | [5 empty] | SWL Adj | 43.7699 | [5 empty] | SWL Adj | 44.5568 |  |  |  |  | SWL Adj | 65.4375 |  |  |  | SWL Adj | 163.686 |  |  |  |  | SWL Adj | #NUM! |  |  |  |  | SWL Adj | #NUM!
| SPL Adj | 32.0705 | [5 empty] | SPL Adj | 31.5214 | [5 empty] | SPL Adj | 30.8892 | [5 empty] | SPL Adj | 30.2339 | [5 empty] | SPL Adj | 29.3729 | [5 empty] | SPL Adj | 28.7699 | [5 empty] | SPL Adj | 29.5568 |  |  |  |  | SPL Adj | 50.4375 |  |  |  | SPL Adj | 148.686 |  |  |  |  | SPL Adj | #NUM! |  |  |  |  | SPL Adj | #NUM!
| Diffuser pressure (design/req) | as above
| MPCD Box Nominal | [6 empty] | MPCD Box Nominal | [6 empty] | MPCD Box Nominal | [6 empty] | MPCD Box Nominal | [6 empty] | MPCD Box Nominal | [6 empty] | MPCD Box Nominal | [6 empty] | MPCD Box Nominal | [5 empty] | MPCD Box Nominal |  |  |  |  | MPCD Box Nominal | [5 empty] | MPCD Box Nominal | [5 empty] | MPCD Box Nominal
MPCD Pressure
| Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 | [5 empty] | Nominal Spigot Diameter | 200 |  |  |  |  | Nominal Spigot Diameter | 200 |  |  |  | Nominal Spigot Diameter | 200 |  |  |  |  | Nominal Spigot Diameter | 200 |  |  |  |  | Nominal Spigot Diameter | 200
| Velocity | 3.2152 | [5 empty] | Velocity | 3.2152 | [5 empty] | Velocity | 3.2152 | [5 empty] | Velocity | 3.2152 | [5 empty] | Velocity | 3.2152 | [5 empty] | Velocity | 3.2152 | [5 empty] | Velocity | 3.2152 |  |  |  |  | Velocity | 3.2152 |  |  |  | Velocity | 3.2152 |  |  |  |  | Velocity | 3.2152 |  |  |  |  | Velocity | 3.2152
| Pd | 6.2024 | [5 empty] | Pd | 6.2024 | [5 empty] | Pd | 6.2024 | [5 empty] | Pd | 6.2024 | [5 empty] | Pd | 6.2024 | [5 empty] | Pd | 6.2024 | [5 empty] | Pd | 6.2024 |  |  |  |  | Pd | 6.2024 |  |  |  | Pd | 6.2024 |  |  |  |  | Pd | 6.2024 |  |  |  |  | Pd | 6.2024
| Pdrop Perf | 5.1068 | [5 empty] | Pdrop Perf | 5.1068 | [5 empty] | Pdrop Perf | 5.1068 | [5 empty] | Pdrop Perf | 5.1068 | [5 empty] | Pdrop Perf | 5.1068 | [5 empty] | Pdrop Perf | 5.1068 | [5 empty] | Pdrop Perf | 5.1068 |  |  |  |  | Pdrop Perf | 5.1068 |  |  |  | Pdrop Perf | 5.1068 |  |  |  |  | Pdrop Perf | 5.1068 |  |  |  |  | Pdrop Perf | 5.1068
| Static Pressure (Inlet) Req | 45.1068 | [5 empty] | Static Pressure (Inlet) Req | 45.1068 | [5 empty] | Static Pressure (Inlet) Req | 45.1068 | [5 empty] | Static Pressure (Inlet) Req | 45.1068 | [5 empty] | Static Pressure (Inlet) Req | 45.1068 | [5 empty] | Static Pressure (Inlet) Req | 45.1068 | [5 empty] | Static Pressure (Inlet) Req | 47.5631 |  |  |  |  | Static Pressure (Inlet) Req | 69.1916 |  |  |  | Static Pressure (Inlet) Req | 90.0177 |  |  |  |  | Static Pressure (Inlet) Req | 117.693 |  |  |  |  | Static Pressure (Inlet) Req | 161.4838
| Static Pressure (Inlet) | 45.1068 | [5 empty] | Static Pressure (Inlet) | 45.1068 | [5 empty] | Static Pressure (Inlet) | 45.1068 | [5 empty] | Static Pressure (Inlet) | 45.1068 | [5 empty] | Static Pressure (Inlet) | 45.1068 | [5 empty] | Static Pressure (Inlet) | 45.1068 | [5 empty] | Static Pressure (Inlet) | 47.5631 |  |  |  |  | Static Pressure (Inlet) | 69.1916 |  |  |  | Static Pressure (Inlet) | 90.0177 |  |  |  |  | Static Pressure (Inlet) | 117.693 |  |  |  |  | Static Pressure (Inlet) | 161.4838
| Total Pressure (Inlet) | 51.3091 | [5 empty] | Total Pressure (Inlet) | 51.3091 | [5 empty] | Total Pressure (Inlet) | 51.3091 | [5 empty] | Total Pressure (Inlet) | 51.3091 | [5 empty] | Total Pressure (Inlet) | 51.3091 | [5 empty] | Total Pressure (Inlet) | 51.3091 | [5 empty] | Total Pressure (Inlet) | 53.7655 |  |  |  |  | Total Pressure (Inlet) | 75.394 |  |  |  | Total Pressure (Inlet) | 96.2201 |  |  |  |  | Total Pressure (Inlet) | 123.8954 |  |  |  |  | Total Pressure (Inlet) | 167.6862
| SWL Adj | 43.9952 | [5 empty] | SWL Adj | 43.4461 | [5 empty] | SWL Adj | 42.814 | [5 empty] | SWL Adj | 42.1586 | [5 empty] | SWL Adj | 41.2976 | [5 empty] | SWL Adj | 40.6946 | [5 empty] | SWL Adj | 41.4815 |  |  |  |  | SWL Adj | 62.3622 |  |  |  | SWL Adj | 160.6107 |  |  |  |  | SWL Adj | #NUM! |  |  |  |  | SWL Adj | #NUM!
| SPL Adj | 28.9952 | [5 empty] | SPL Adj | 28.4461 | [5 empty] | SPL Adj | 27.814 | [5 empty] | SPL Adj | 27.1586 | [5 empty] | SPL Adj | 26.2976 | [5 empty] | SPL Adj | 25.6946 | [5 empty] | SPL Adj | 26.4815 |  |  |  |  | SPL Adj | 47.3622 |  |  |  | SPL Adj | 145.6107 |  |  |  |  | SPL Adj | #NUM! |  |  |  |  | SPL Adj | #NUM!
| SWL Throttle Adj | 45.4396
| SPL Throttle Adj | 30.4396
| MPCD Box small | [6 empty] | MPCD Box small | [6 empty] | MPCD Box small | [6 empty] | MPCD Box small | [6 empty] | MPCD Box small | [6 empty] | MPCD Box small | [6 empty] | MPCD Box small | [5 empty] | MPCD Box small |  |  |  |  | MPCD Box small | [5 empty] | MPCD Box small | [5 empty] | MPCD Box small
| Nominal Spigot Diameter | FALSE | [5 empty] | Nominal Spigot Diameter | FALSE | [5 empty] | Nominal Spigot Diameter | FALSE | [5 empty] | Nominal Spigot Diameter | FALSE | [5 empty] | Nominal Spigot Diameter | FALSE | [5 empty] | Nominal Spigot Diameter | FALSE | [5 empty] | Nominal Spigot Diameter | FALSE |  |  |  |  | Nominal Spigot Diameter | FALSE |  |  |  | Nominal Spigot Diameter | FALSE |  |  |  |  | Nominal Spigot Diameter | FALSE |  |  |  |  | Nominal Spigot Diameter | FALSE
| Velocity | 5.7351 | [5 empty] | Velocity | 5.7351 | [5 empty] | Velocity | 5.7351 | [5 empty] | Velocity | 5.7351 | [5 empty] | Velocity | 5.7351 | [5 empty] | Velocity | 5.7351 | [5 empty] | Velocity | 5.7351 |  |  |  |  | Velocity | 5.7351 |  |  |  | Velocity | 5.7351 |  |  |  |  | Velocity | 5.7351 |  |  |  |  | Velocity | 5.7351
| Pd | 19.7345 | [5 empty] | Pd | 19.7345 | [5 empty] | Pd | 19.7345 | [5 empty] | Pd | 19.7345 | [5 empty] | Pd | 19.7345 | [5 empty] | Pd | 19.7345 | [5 empty] | Pd | 19.7345 |  |  |  |  | Pd | 19.7345 |  |  |  | Pd | 19.7345 |  |  |  |  | Pd | 19.7345 |  |  |  |  | Pd | 19.7345
| Pdrop Perf | 12.422 | [5 empty] | Pdrop Perf | 12.422 | [5 empty] | Pdrop Perf | 12.422 | [5 empty] | Pdrop Perf | 12.422 | [5 empty] | Pdrop Perf | 12.422 | [5 empty] | Pdrop Perf | 12.422 | [5 empty] | Pdrop Perf | 12.422 |  |  |  |  | Pdrop Perf | 12.422 |  |  |  | Pdrop Perf | 12.422 |  |  |  |  | Pdrop Perf | 12.422 |  |  |  |  | Pdrop Perf | 12.422
| Static Pressure (Inlet) Req | 52.422 | [5 empty] | Total Pressure (Inlet) Req | 52.422 | [5 empty] | Total Pressure (Inlet) Req | 52.422 | [5 empty] | Total Pressure (Inlet) Req | 52.422 | [5 empty] | Total Pressure (Inlet) Req | 52.422 | [5 empty] | Total Pressure (Inlet) Req | 52.422 | [5 empty] | Total Pressure (Inlet) Req | 54.8783 |  |  |  |  | Total Pressure (Inlet) Req | 76.5068 |  |  |  | Total Pressure (Inlet) Req | 97.3329 |  |  |  |  | Total Pressure (Inlet) Req | 125.0082 |  |  |  |  | Total Pressure (Inlet) Req | 168.799
| Static Pressure (Inlet) | 52.422 | [5 empty] | Static Pressure (Inlet) | 52.422 | [5 empty] | Static Pressure (Inlet) | 52.422 | [5 empty] | Static Pressure (Inlet) | 52.422 | [5 empty] | Static Pressure (Inlet) | 52.422 | [5 empty] | Static Pressure (Inlet) | 52.422 | [5 empty] | Static Pressure (Inlet) | 54.8783 |  |  |  |  | Static Pressure (Inlet) | 76.5068 |  |  |  | Static Pressure (Inlet) | 97.3329 |  |  |  |  | Static Pressure (Inlet) | 125.0082 |  |  |  |  | Static Pressure (Inlet) | 168.799
| Total Pressure (Inlet) | 72.1565 | [5 empty] | Total Pressure (Inlet) | 72.1565 | [5 empty] | Total Pressure (Inlet) | 72.1565 | [5 empty] | Total Pressure (Inlet) | 72.1565 | [5 empty] | Total Pressure (Inlet) | 72.1565 | [5 empty] | Total Pressure (Inlet) | 72.1565 | [5 empty] | Total Pressure (Inlet) | 74.6128 |  |  |  |  | Total Pressure (Inlet) | 96.2413 |  |  |  | Total Pressure (Inlet) | 117.0674 |  |  |  |  | Total Pressure (Inlet) | 144.7427 |  |  |  |  | Total Pressure (Inlet) | 188.5336
| SWL Adj | 47.8557 | [5 empty] | SWL Adj | 47.3065 | [5 empty] | SWL Adj | 46.6744 | [5 empty] | SWL Adj | 46.0191 | [5 empty] | SWL Adj | 45.1581 | [5 empty] | SWL Adj | 44.5551 | [5 empty] | SWL Adj | 45.342 |  |  |  |  | SWL Adj | 66.2227 |  |  |  | SWL Adj | 164.4711 |  |  |  |  | SWL Adj | #NUM! |  |  |  |  | SWL Adj | #NUM!
| SPL Adj | 32.8557 | [5 empty] | SPL Adj | 32.3065 | [5 empty] | SPL Adj | 31.6744 | [5 empty] | SPL Adj | 31.0191 | [5 empty] | SPL Adj | 30.1581 | [5 empty] | SPL Adj | 29.5551 | [5 empty] | SPL Adj | 30.342 |  |  |  |  | SPL Adj | 51.2227 |  |  |  | SPL Adj | 149.4711 |  |  |  |  | SPL Adj | #NUM! |  |  |  |  | SPL Adj | #NUM!
| SWL Throttle Adj | 49.1151
| SPL Throttle Adj | 34.1151
Throttled MPCD Adjustments
| Static P_throttled | 55.1068
| Total Pressure (Inlet) | 61.3091
| P_throttle ratio static | 1.2217
| SWL Adj | 1.4444
| Static P_throttled | 62.422
| Total Pressure (Inlet) | 82.1565
| P_throttle ratio static | 1.1908
| SWL Adj | 1.2594
| D0 | [6 empty] | D1 | [6 empty] | D2 | [6 empty] | D3 | [6 empty] | D4 | [6 empty] | D5 | [6 empty] | D6 | [5 empty] | D7 |  |  |  |  | D8 | [5 empty] | D9 | [5 empty] | D10
| Global Distances | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| Cmax | 8.4 | 8.5 | 8.7 | 8.8 | 9.2 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3
| Cmin | 2.3 | 2.3 | 2.4 | 2.4 | 2.4 | 2.5 | 2.6 | 2.7 | 2.9 | 3.1 | 3.4
| Gray Column | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE
| Cmax | 4: 9.2; 5: 9.3
| Cmin | 4: 2.4; 5: 2.5
| Total Avg | 0: 5.85
| Case 1 Avg v'' | 0: 2.9221
| Case 2 v'' | 0: 2.7778
| Specified Specific Flowrate | 0: 2.6
| V'' | 0: 2.9
| v" unit converted for display | 0: 2.9
| V'' for heating | 0: 2.9
| C Selected | 0: 5.9
| max spec fr | 0: 30
Spigot
| Perf | 0: 52%
| K = | 0: -53.75
| zeta perf | 0: 3.4784
| Max Spigot Velocity | 0: 3.5; 1: m/s
| Max Spigot Velocity Max Buffer | 0: 3.8; 1: m/s
Spigot Selection Vari-Swirl
|  | 0: High Profile 350; D1 8: Standard Box 250 | [5 empty] | Ultra-Low Box 200 ??? | [7 empty] | MPCD Box | [12 empty] | MPCD Box
|  | DN | Max Airflow | Selection | Spigot Area (reduced) | round | squish factor | Squish Ratio |  | DN | Max Airflow | Selection | Spigot Area (reduced) | round | squish factor | Squish ratio |  | DN | Max Airflow | Selection | Spigot Area (reduced) | round | squish factor | Squish Ratio |  | DN | Max Airflow | Selection | Spigot Area (round) | box height | squish factor | Squish Ratio | [6 empty] | DN | Max Airflow | Selection | Spigot Area (round) | box height | squish factor | Squish Ratio
| 1 | 150 | 62 | 0 | 0.017437 | TRUE | 0 | 1 | 1 | 150 | 62 | 0 | 0.017437 | TRUE | 0 | 1 | 1 | 150 | 59 | 0 | 0.016654 |  | 0 | 1.304 | 1 | 150 | 62 | 0 | 0.017437 | 250 | 0 | 1.304 | [5 empty] | 1 | 150 | 62 | 0 | 0.017437 | 250 | 0 | 1.304
| 2 | 200 | 109 | 1 | 0.031103 | TRUE | 0 | 1 | 2 | 200 | 107 | 1 | 0.030293 | FALSE | 0 | 1.2171 | 2 | 200 | 87 | 0 | 0.024754 |  | 0.428 | 1.928 | 2 | 200 | 109 | 1 | 0.031103 | 300 | 0.428 | 1.928 | [5 empty] | 2 | 200 | 109 | 1 | 0.031103 | 300 | 0.428 | 1.928
| 3 | 250 | 171 | 1 | 0.048695 | TRUE | 0 | 1 | 3 | 250 | 147 | 1 | 0.042 | FALSE | 0.16286 | 1.6629 | 3 | 250 | 114 | 1 | 0.03232 |  | 1.06 | 2.56 | 3 | 250 | 171 | 1 | 0.048695 | 350 | 1.06 | 2.56 | [5 empty] | 3 | 250 | 171 | 1 | 0.048695 | 350 | 1.06 | 2.56
| 4 | 300 | 235 | 1 | 0.066961 | FALSE | 0 | 1.252 | 4 | 300 | 186 | 1 | 0.052908 | FALSE | 0.61429 | 2.1143 | 4 | 300 | 139 | 1 | 0.039658 |  | 1.684 | 3.184 | 4 | 300 | 246 | 1 | 0.070215 | 400 | 1.684 | 3.184 | [5 empty] | 4 | 300 | 246 | 1 | 0.070215 | 400 | 1.684 | 3.184
| 5 | 350 | 293 | 1 | 0.083559 | FALSE | 0 | 1.624 | 5 | 350 | 223 | 1 | 0.06343 | FALSE | 1.06 | 2.56 | 5 | N/A | [6 empty] | 5 | N/A | [11 empty] | 5 | N/A
| 6 | 0: N/A; D1 7: 6; D1 8: N/A
|  | 1: Standard; 2: 2; D1 9: Standard; D1 10: 2 | [6 empty] | Ultra-Low | 3 | [6 empty] | MPCD Box | 2 | 300 |  |  |  | MPCD Box-1 | 1 | 250 |  |  |  |  | MPCD Box | 2 | 300 |  |  |  | MPCD Box-1 | 1 | 250
|  | 1: Spigot; 2: 200; D1 9: Spigot; D1 10: 200 | [6 empty] | Spigot | 250 | [6 empty] | Spigot | 200 | H300 |  |  |  | Spigot | 150 | H250 |  |  |  |  | Spigot | 200 | H300 |  |  |  | Spigot | 150 | H250
|  | 1: Spigot Area; 2: 0.031103; D1 9: Spigot Area; D1 10: 0.030293 | [6 empty] | Spigot Area | 0.03232 | [6 empty] | Spigot Area | 0.031103 |  |  |  |  | Spigot Area | 0.017437 | [5 empty] | Spigot Area | 0.031103 |  |  |  |  | Spigot Area | 0.017437
|  | 1: Velocity; 2: 3.2152; D1 9: Velocity; D1 10: 3.3011 | [6 empty] | Velocity | 3.0941 | [6 empty] | Velocity | 3.2152 |  |  |  |  | Velocity | 5.7351 | [5 empty] | Velocity | 3.2152 |  |  |  |  | Velocity | 5.7351
|  | 1: Box X-sect A; 2: 0.1815; D1 9: Box X-sect A; D1 10: 0.1265 | [6 empty] | Box X-sect A | 0.099 | [6 empty] | Box X-sect A | 0.154 |  |  |  |  | Box X-sect A | 0.1265 | [5 empty] | Box X-sect A | 0.154 |  |  |  |  | Box X-sect A | 0.1265
|  | 1: DN:H A Ratio; 2: 0.17136; D1 9: DN:H A Ratio; D1 10: 0.23947 | [6 empty] | DN:H A Ratio | 0.32646 | [6 empty] | DN:H A Ratio | 0.20196 |  |  |  |  | DN:H A Ratio | 0.13784 | [5 empty] | DN:H A Ratio | 0.20196 |  |  |  |  | DN:H A Ratio | 0.13784
|  | 1: Ax; 2: 4.387; D1 9: Ax; D1 10: 4.8107 | [6 empty] | Ax | 5.3518 | [6 empty] | Ax | 4.5774 |  |  |  |  | Ax | 4.1785 | [5 empty] | Ax | 4.5774 |  |  |  |  | Ax | 4.1785
|  | 1: b; 2: -0.68783; D1 9: b; D1 10: -0.65979 | [6 empty] | b | -0.62396 | [6 empty] | b | -0.67523 |  |  |  |  | b | -0.70164 | [5 empty] | b | -0.67523 |  |  |  |  | b | -0.70164
|  | 1: P(DN:H) Ratio; 2: 0.18472; D1 9: P(DN:H) Ratio; D1 10: 0.23048 | [6 empty] | P(DN:H) Ratio | 0.30239 | [6 empty] | P(DN:H) Ratio | 0.20425 |  |  |  |  | P(DN:H) Ratio | 0.1651 | [5 empty] | P(DN:H) Ratio | 0.20425 |  |  |  |  | P(DN:H) Ratio | 0.1651
|  | 1: P(H:DN) Ratio; 2: 0.81528; D1 9: P(H:DN Tatio; D1 10: 0.76952 | [6 empty] | P(H:DN Tatio | 0.69761 | [6 empty] | P(H:DN Tatio | 0.79575 |  |  |  |  | P(H:DN Tatio | 0.8349 | [5 empty] | P(H:DN Tatio | 0.79575 |  |  |  |  | P(H:DN Tatio | 0.8349
|  | 1: P(DN/perf); 2: 21.5744; D1 9: P(DN/perf); D1 10: 22.7428 | [6 empty] | P(DN/perf) | 19.9799 | [6 empty] | P(DN/perf) | 21.5744 |  |  |  |  | P(DN/perf) | 68.6445 | [5 empty] | P(DN/perf) | 21.5744 |  |  |  |  | P(DN/perf) | 68.6445
|  | 1: P(H/perf); 2: 0.63354; D1 9: P(H/perf); D1 10: 1.3042 | [6 empty] | P(H/perf) | 2.1294 | [6 empty] | P(H/perf) | 0.88001 |  |  |  |  | P(H/perf) | 1.3042 | [5 empty] | P(H/perf) | 0.88001 |  |  |  |  | P(H/perf) | 1.3042
|  | 1: Pdrop Perf; 2: 4.5017; D1 9: Pdrop Perf; D1 10: 6.2454 | [6 empty] | Pdrop Perf | 7.5273 | [6 empty] | Pdrop Perf | 5.1068 |  |  |  |  | Pdrop Perf | 12.422 | [5 empty] | Pdrop Perf | 5.1068 |  |  |  |  | Pdrop Perf | 12.422
|  | 1: SWL Squish Factor; 2: 0; 3: hard coded 0; D1 9: SWL Squish Factor; D1 10: 0 | hard coded 0 | [5 empty] | SWL Squish Factor | 3 | hard coded 3 | [5 empty] | SWL Squish Factor | 0 | hard coded 0 |  |  |  | SWL Squish Factor | 0 | hard coded 0 |  |  |  |  | SWL Squish Factor | 0 | hard coded 0 |  |  |  | SWL Squish Factor | 0 | hard coded 0
|  | 1: SWL Adj; 2: 0; D1 9: SWL Adj; D1 10: 1.4219 | [6 empty] | SWL Adj | 5.2327 | [6 empty] | SWL Adj | 2.1574 | Includes Damper Noise Increase |  |  |  | SWL Adj | 6.0178 | Includes Damper Noise Increase |  |  |  |  | SWL Adj | 2.1574 | Includes Damper Noise Increase |  |  |  | SWL Adj | 6.0178 | Includes Damper Noise Increase
|  | 0: Noise; D1 8: Noise | [5 empty] | Noise | [7 empty] | Noise | [5 empty] | Noise | [6 empty] | Noise | [5 empty] | Noise
|  | 0: Spigot; 1: Qspigot; 2: 18.4716; D1 8: Spigot; D1 9: Qspigot; D1 10: 23.048 | [5 empty] | Spigot | Qspigot | 30.2393 | [5 empty] | Spigot | Qspigot | 20.4246 |  |  |  | Spigot | Qspigot | 16.5098 |  |  |  |  | Spigot | Qspigot | 20.4246 |  |  |  | Spigot | Qspigot | 16.5098
|  | 1: v.h =; 2: 1.1421; D1 9: v.h =; D1 10: 1.4631 | [6 empty] | v.h = | 1.7993 | [6 empty] | v.h = | 1.2629 |  |  |  |  | v.h = | 1.8209 | [5 empty] | v.h = | 1.2629 |  |  |  |  | v.h = | 1.8209
|  | 1: holes; 2: 3294.6277; D1 9: holes; D1 10: 3208.8808 | [6 empty] | holes | 3423.5665 | [6 empty] | holes | 3294.6277 |  |  |  |  | holes | 1847.0248 | [5 empty] | holes | 3294.6277 |  |  |  |  | holes | 1847.0248
|  | 1: dLw =; 2: 35.057; D1 9: dLw =; D1 10: 34.9429 | [6 empty] | dLw = | 35.2232 | [6 empty] | dLw = | 35.057 |  |  |  |  | dLw = | 32.5523 | [5 empty] | dLw = | 35.057 |  |  |  |  | dLw = | 32.5523
|  | 1: SWL1; 2: -14.574; D1 9: SWL1; D1 10: -7.009 | [6 empty] | SWL1 | -0.3178 | [6 empty] | SWL1 | -11.4583 |  |  |  |  | SWL1 | -2.619 | [5 empty] | SWL1 | -11.4583 |  |  |  |  | SWL1 | -2.619
|  | 0: x-sect; 1: Qx-sect; 2: 81.5284; D1 8: x-sect; D1 9: Qx-sect; D1 10: 76.952 | [5 empty] | x-sect | Qx-sect | 69.7607 | [5 empty] | x-sect | Qx-sect | 79.5754 |  |  |  | x-sect | Qx-sect | 83.4902 |  |  |  |  | x-sect | Qx-sect | 79.5754 |  |  |  | x-sect | Qx-sect | 83.4902
|  | 1: v.h =; 2: 0.86383; D1 9: v.h =; D1 10: 1.1698 | [6 empty] | v.h = | 1.3551 | [6 empty] | v.h = | 0.9937 |  |  |  |  | v.h = | 1.2692 | [5 empty] | v.h = | 0.9937 |  |  |  |  | v.h = | 1.2692
|  | 1: holes; 2: 19225.9116; D1 9: holes; D1 10: 13399.8778 | [6 empty] | holes | 10486.8609 | [6 empty] | holes | 16312.8947 |  |  |  |  | holes | 13399.8778 | [5 empty] | holes | 16312.8947 |  |  |  |  | holes | 13399.8778
|  | 1: dLw =; 2: 42.6915; D1 9: dLw =; D1 10: 41.129 | [6 empty] | dLw = | 40.0681 | [6 empty] | dLw = | 41.9803 |  |  |  |  | dLw = | 41.129 | [5 empty] | dLw = | 41.9803 |  |  |  |  | dLw = | 41.129
|  | 1: SWL2; 2: -15.5963; D1 9: SWL2; D1 10: -7.7582 | [6 empty] | SWL2 | -4.2617 | [6 empty] | SWL2 | -11.9656 |  |  |  |  | SWL2 | -5.2302 | [5 empty] | SWL2 | -11.9656 |  |  |  |  | SWL2 | -5.2302
|  | 1: Sum; 2: -15.3884; D1 9: Sum; D1 10: -7.5737 | 7.8147 | [5 empty] | Sum | 1.1537 | 16.5421 | [5 empty] | Sum | -8.6943 | -1.1206 |  |  |  | Sum | -0.72097 | -0.72097 |  |  |  |  | Sum | -8.6943 | -8.6943 |  |  |  | Sum | -0.72097 | -0.72097
|  | 1: diffuser sum; 2: 41; D1 10: 41.0001 | [7 empty] | 41.0002 | [7 empty] | 41 | [5 empty] | 41.0001 | [6 empty] | 41 | [5 empty] | 41.0001
|  | 2: 41; D1 10: 41.0001 | 5.0338e-05 | [6 empty] | 41.0004 | 0.00043994 | [6 empty] | 41 | -1.3717e-05 |  |  |  |  | 41.0003 | 41.0003 | [5 empty] | 41 | 41 |  |  |  |  | 41.0003 | 41.0003
[26 empty] | Pressure Damper SWL Adjustment | [5 empty] | Pressure Damper SWL Adjustment | [6 empty] | Pressure Damper SWL Adjustment | [5 empty] | Pressure Damper SWL Adjustment
| Normal Box Selection | [24 empty] | dP | 0 |  |  |  |  | dP | 0 | [5 empty] | dP | 0 |  |  |  |  | dP | 0
| Box Selection | 0: Airflow Max; 1: Airflow Min | [13 empty] | Pressure Ratio% | 1.25 |  |  |  |  | Pressure Ratio% | 1.25 | [5 empty] | Pressure Ratio% | 1.25 |  |  |  |  | Pressure Ratio% | 1.25
| H350 | 0: 300; 1: 186; 3: at 44 dba | [13 empty] | SWL increase | 1.6096 |  |  |  |  | SWL increase | 1.6096 | [5 empty] | SWL increase | 1.6096 |  |  |  |  | SWL increase | 1.6096
| H250 | 0: 186; 1: 87; 3: 37.4 dba
| H200 | 0: 87; 1: 0
Recommended | H250 | 0: 2 | [11 empty] | https://www.aivc.org/sites/default/files/members_area/medias/pdf/CR/CR02_Flow_generated_noise.pdf
Recommended | 250 | [22 empty] | damper throttled % | velocity increase | pressure increase | SWL increase
[24 empty] | 100 | 1 | 1 | 0
| Acoustic min max | 1: Box | [11 empty] | 70.7107 | 1.4142 | 2 | 5
[24 empty] | 50 | 2 | 4 | 10
https://strutt.arup.com/help/Mechanical_Services/DamperRegen.htm
MPCD Box Selection
| Box Selection | 0: Spigot; 1: Airflow Max; 2: Airflow Min
| H400 | 0: DN300; 1: 246; 2: 171
| H350 | 0: DN250; 1: 171; 2: 109
| H300 | 0: DN200; 1: 109; 2: 62
| H250 | 0: DN150; 1: 62; 2: 0
Recommended | H300 | 0: DN200; 1: 3
Recommended | 300 | 0: 200
Undersized MPCD Spigot DISPLAY TRUE/FALS
Undersize Selection | FALSE
Undersized | Box | 0: Spigot
Text | N/A | 0: N/A
Number | N/A | 0: N/A
[20 empty] | Flow Rate | Pressure | Door | Damper Position | SWL | Comment
[20 empty] | 120 | 30 (60) | D3 | 81% | 41 | with pressure relief damper
Box Selection | Box Size | 0: Spigot | [7 empty] | 120 | 30 | D3 | 81% | 36 | standard 30 Pa good design
| H250 | 0: 2 | [7 empty] | 120 | 60 | D3 | 54% | 45.3 | no pressure relief damper
Collated Results
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
| Max Recommended Airflow | 253.8686 | 213.0733 | 179.4604 | 156.5491 | 131.4517 | 116.4631 | 97.0641 | 79.0046 | 68.6354 | 59.6056 | 50.5759
| Selected Airflow | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Selected Pressure | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| Door Pos @ 100% V and design pressure | 27% | 34% | 44% | 55% | 67% | 78% | 104% | 163% | 238% | 751% | 1033%
| Static Pressure at 100% Damper | 6.2064 | 8.8105 | 12.42 | 16.3215 | 23.1488 | 29.4906 | 42.4563 | 64.0848 | 84.9109 | 112.5862 | 156.3771
| Min % TD to | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 0.3 | 0.3 | 0.3 | 0.3
| Min Selected Airflow | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Min Permissible % Turndown to | 21.99% | 18.45% | 15.54% | 13.56% | 11.38% | 10.09% | 10% | 0.1 | 0.1 | 0.1 | 0.1
| Min Permissible Airflow | 21.9857 | 18.4527 | 15.5417 | 13.5575 | 11.384 | 10.086 | 10 | 10 | 10 | 10 | 10
| ΔT_max centre | 8.3474 | 9.3662 | 10.3861 | 11.1749 | 12.1228 | 12.8667 | 13.6908 | 14.5556 | 15.058 | 15.5269 | 16.0099
| ΔT_max (heating) | 5.5649 | 6.2442 | 6.924 | 7.4499 | 8.0818 | 8.5778 | 9.1272 | 9.7037 | 10.0387 | 10.3513 | 10.6733
| Cmax (centre) | 8.3799 | 8.4926 | 8.6566 | 8.8449 | 9.2064 | 9.2582 | 9.2582 | 9.2582 | 9.2582 | 9.2582 | 9.2582
| Cmax (perimeter) | 7.5339 | 7.6352 | 7.7826 | 7.952 | 8.277 | 8.6175 | 9.2582 | 9.2582 | 9.2582 | 9.2582 | 9.2582
| Cmin | 2.289 | 2.3194 | 2.3565 | 2.3925 | 2.4496 | 2.4985 | 2.5918 | 2.7386 | 2.8782 | 3.0693 | 3.4023
| Hmin | 2.2471 | 2.2471 | 2.2471 | 2.2471 | 2.2471 | 2.2471 | 2.2471 | 2.3471 | 2.3471 | 2.3471 | 2.3471
| air velocity | 0.10668 | 0.10879 | 0.11085 | 0.11273 | 0.11546 | 0.1176 | 0.12123 | 0.12564 | 0.12934 | 0.13345 | 0.13878
| Draft Rating | 8.757% | 0.090168 | 0.092714 | 0.095023 | 0.098389 | 0.10102 | 0.1055 | 11.09% | 11.55% | 12.06% | 12.73%
| PPD | 5.573% | 0.056607 | 0.057476 | 0.05827 | 0.059437 | 0.060358 | 0.061941 | 6.389% | 6.556% | 6.744% | 6.993%
PMV | bar: 0 to 10
| PPD class | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3
| 350mm box Spigot D | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| Static Pressure | 44.5017 | 44.5017 | 44.5017 | 44.5017 | 44.5017 | 44.5017 | 46.958 | 68.5865 | 89.4126 | 117.0879 | 160.8787
| Total Pressure Adj | 50.704 | 50.704 | 50.704 | 50.704 | 50.704 | 50.704 | 53.1604 | 74.7889 | 95.615 | 123.2903 | 167.0811
| SWL Adj | 41.8378 | 41.2887 | 40.6566 | 40.0012 | 39.1403 | 38.5372 | 39.3241 | 60.2048 | 158.4533 | #NUM! | #NUM!
| SPL Adj | 26.8378 | 26.2887 | 25.6566 | 25.0012 | 24.1403 | 23.5372 | 24.3241 | 45.2048 | 143.4533 | #NUM! | #NUM!
| 250mm box spigot | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| Static Pressure | 46.2454 | 46.2454 | 46.2454 | 46.2454 | 46.2454 | 46.2454 | 48.7017 | 70.3302 | 91.1563 | 118.8316 | 162.6224
| Total Pressure Adj | 52.7837 | 52.7837 | 52.7837 | 52.7837 | 52.7837 | 52.7837 | 55.24 | 76.8685 | 97.6946 | 125.3699 | 169.1607
| SWL Adj | 43.2597 | 42.7106 | 42.0784 | 41.4231 | 40.5621 | 39.9591 | 40.746 | 61.6267 | 159.8752 | #NUM! | #NUM!
| SPL Adj | 28.2597 | 27.7106 | 27.0784 | 26.4231 | 25.5621 | 24.9591 | 25.746 | 46.6267 | 144.8752 | #NUM! | #NUM!
| 200mm box Spigot D | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
| Static Pressure | 57.5273 | 47.5273 | 47.5273 | 47.5273 | 47.5273 | 47.5273 | 49.9836 | 71.6121 | 92.4382 | 120.1135 | 163.9043
| Total Pressure Adj | 63.2713 | 53.2713 | 53.2713 | 53.2713 | 53.2713 | 53.2713 | 55.7276 | 77.3561 | 98.1822 | 125.8575 | 169.6483
| SWL Adj | 47.0705 | 46.5214 | 45.8892 | 45.2339 | 44.3729 | 43.7699 | 44.5568 | 65.4375 | 163.686 | #NUM! | #NUM!
| SPL Adj | 32.0705 | 31.5214 | 30.8892 | 30.2339 | 29.3729 | 28.7699 | 29.5568 | 50.4375 | 148.686 | #NUM! | #NUM!
| MPCD box nom Spigot D | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| Static Pressure | 45.1068 | 45.1068 | 45.1068 | 45.1068 | 45.1068 | 45.1068 | 47.5631 | 69.1916 | 90.0177 | 117.693 | 161.4838
| Total Pressure Adj | 51.3091 | 51.3091 | 51.3091 | 51.3091 | 51.3091 | 51.3091 | 53.7655 | 75.394 | 96.2201 | 123.8954 | 167.6862
| SWL Adj | 43.9952 | 43.4461 | 42.814 | 42.1586 | 41.2976 | 40.6946 | 41.4815 | 62.3622 | 160.6107 | #NUM! | #NUM!
| SPL Adj | 28.9952 | 28.4461 | 27.814 | 27.1586 | 26.2976 | 25.6946 | 26.4815 | 47.3622 | 145.6107 | #NUM! | #NUM!
| MPCD box smal Spigot D | 150 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| Static Pressure | 52.422 | 52.422 | 52.422 | 52.422 | 52.422 | 52.422 | 54.8783 | 76.5068 | 97.3329 | 125.0082 | 168.799
| Total Pressure Adj | 72.1565 | 72.1565 | 72.1565 | 72.1565 | 72.1565 | 72.1565 | 74.6128 | 96.2413 | 117.0674 | 144.7427 | 188.5336
| SWL Adj | 47.8557 | 47.3065 | 46.6744 | 46.0191 | 45.1581 | 44.5551 | 45.342 | 66.2227 | 164.4711 | #NUM! | #NUM!
| SPL Adj | 32.8557 | 32.3065 | 31.6744 | 31.0191 | 30.1581 | 29.5551 | 30.342 | 51.2227 | 149.4711 | #NUM! | #NUM!
Syntax & Format
|  | D0 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | D9 | D10
| Max Recommended Airflow | 254 | 213 | 179 | 157 | 131 | 116 | 97 | 79 | 69 | 60 | 51
| Selected Airflow | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Selected Pressure | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| Door Pos @ 100% V and design pressure | 27% | 34% | 44% | 55% | 67% | 78% | - | - | - | - | -
| Static Pressure at 100% Damper | 6.2 | 8.8 | 12.4 | 16.3 | 23.1 | 29.5 | 42.5 | 64.1 | 84.9 | 112.6 | 156.4
| Min % TD to | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| Min Airflow | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Min Permissible % Turndown to | 22% | 18.5% | 15.5% | 13.6% | 11.4% | 10.1% | 10% | 10% | 10% | 10% | 10%
| Min Permissible Airflow | 22 | 18.5 | 15.5 | 13.6 | 11.4 | 10.1 | 10 | 10 | 10 | 10 | 10
| ΔT_max centre | 8.3 | 9.4 | 10.4 | 11.2 | 12.1 | 12.9 | 13.7 | 14.6 | 15 | 15 | 15
| ΔT_max (heating) perimeter | 5.6 | 6.2 | 6.9 | 7.4 | 8.1 | 8.6 | 9.1 | 9.7 | 10 | 10.4 | 10.7
| Cmax (centre) | 8.4 | 8.5 | 8.7 | 8.8 | 9.2 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3
| Cmax (perimeter) | 7.5 | 7.6 | 7.8 | 8 | 8.3 | 8.6 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3
| Cmin | 2.3 | 2.3 | 2.4 | 2.4 | 2.4 | 2.5 | 2.6 | 2.7 | 2.9 | 3.1 | 3.4
| Hmin | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.3 | 2.3 | 2.3 | 2.3
| air velocity | 0.11 | 0.11 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.13 | 0.13 | 0.13 | 0.14
| Draft Rating | 0.088 | 0.09 | 0.093 | 0.095 | 0.098 | 0.101 | 0.106 | 0.111 | 0.116 | 0.121 | 0.127
| PPD | 0.056 | 0.057 | 0.057 | 0.058 | 0.059 | 0.06 | 0.062 | 0.064 | 0.066 | 0.067 | 0.07
PPD Cat | bar: D0 to D10
| PMV | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.3 | < 0.3 | < 0.3
| 350 mm High-Profile Connection Box | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200
| Static Pressure | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 47 | 68.6 | 89.4 | 117.1 | 160.9
| Total Pressure Adj | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 53.2 | 74.8 | 95.6 | 123.3 | 167.1
| SWL Adj | 41.8 | 41.3 | 40.7 | 40 | 39.1 | 38.5 | 39.3 | 60.2 | - | - | -
| SPL Adj | 26.8 | 26.3 | 25.7 | 25 | 24.1 | 23.5 | 24.3 | 45.2 | - | - | -
| 250 mm Medium-Profile Connection Box | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200
| Static Pressure | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 48.7 | 70.3 | 91.2 | 118.8 | 162.6
| Total Pressure | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 55.2 | 76.9 | 97.7 | 125.4 | 169.2
| SWL Adj | 43.3 | 42.7 | 42.1 | 41.4 | 40.6 | 40 | 40.7 | 61.6 | - | - | -
| SPL Adj | 28.3 | 27.7 | 27.1 | 26.4 | 25.6 | 25 | 25.7 | 46.6 | - | - | -
| 200 mm Low-Profile Connection Box | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250
| Static Pressure | 57.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 50 | 71.6 | 92.4 | 120.1 | 163.9
| Total Pressure | 63.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 55.7 | 77.4 | 98.2 | 125.9 | 169.6
| SWL Adj | 47.1 | 46.5 | 45.9 | 45.2 | 44.4 | 43.8 | 44.6 | 65.4 | - | - | -
| SPL Adj | 32.1 | 31.5 | 30.9 | 30.2 | 29.4 | 28.8 | 29.6 | 50.4 | - | - | -
| 300 mm High Round Spigot Connection Box | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200
| Static Pressure | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 47.6 | 69.2 | 90 | 117.7 | 161.5
| Total Pressure Adj | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 53.8 | 75.4 | 96.2 | 123.9 | 167.7
| SWL Adj | 44 | 43.4 | 42.8 | 42.2 | 41.3 | 40.7 | 41.5 | 62.4 | - | - | -
| SPL Adj | 29 | 28.4 | 27.8 | 27.2 | 26.3 | 25.7 | 26.5 | 47.4 | - | - | -
Static Pressure
Total Pressure Adj
SWL Adj
SPL Adj
Final Result Size Selection
0 | Selection? | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | Door | D0 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | D9 | D10
2 | Airflow @ 100% Damper and 40 Pa | 254 | 213 | 179 | 157 | 131 | 116 | 97 | 79 | 69 | 60 | 51
3 | Max Airflow | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
4 | Selected Design Pressure | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0
5 | Damper Position at 100 L/s and 40 Pa | 27% | 34% | 44% | 55% | 67% | 78% | - | - | - | - | -
6 | Static Pressure @ 100% Airflow [Pa] | 6.2 | 8.8 | 12.4 | 16.3 | 23.1 | 29.5 | 42.5 | 64.1 | 84.9 | 112.6 | 156.4
7 | Selected Turndown to | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
8 | Min Selected Airflow | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
9 | Min Permissible % Turndown to | 0.22 | 0.185 | 0.155 | 0.136 | 0.114 | 0.101 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
10 | Min Permissible Airflow | 22 | 18.5 | 15.5 | 13.6 | 11.4 | 10.1 | 10 | 10 | 10 | 10 | 10
11 | Max ΔT (heating) - Centre Zone [K] | 8.3 | 9.4 | 10.4 | 11.2 | 12.1 | 12.9 | 13.7 | 14.6 | 15 | 15 | 15
12 | Max ΔT (heating) - Perimeter [K] | 5.6 | 6.2 | 6.9 | 7.4 | 8.1 | 8.6 | 9.1 | 9.7 | 10 | 10.4 | 10.7
13 | Max Centreline Distance (centre) [m] | 8.4 | 8.5 | 8.7 | 8.8 | 9.2 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3
14 | Max Centreline Distance Perimeter [m] | 7.5 | 7.6 | 7.8 | 8 | 8.3 | 8.6 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3
15 | Min Centreline Distance [m] | 2.3 | 2.3 | 2.4 | 2.4 | 2.4 | 2.5 | 2.6 | 2.7 | 2.9 | 3.1 | 3.4
16 | Min Permissible Diffuser Height [m] | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.3 | 2.3 | 2.3 | 2.3
17 | Mean Room Air Velocity [m/s] | 0.11 | 0.11 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.13 | 0.13 | 0.13 | 0.14
18 | Mean Draught Rating (DR) | 0.088 | 0.09 | 0.093 | 0.095 | 0.098 | 0.101 | 0.106 | 0.111 | 0.116 | 0.121 | 0.127
19 | Mean PPD | 0.056 | 0.057 | 0.057 | 0.058 | 0.059 | 0.06 | 0.062 | 0.064 | 0.066 | 0.067 | 0.07
20 | Satisfies PPD Category (ISO7730) | bar: 0 to 10
21 | PMV | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.2 | < 0.3 | < 0.3 | < 0.3
22 | 350 mm High-Profile Connection Box | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200
23 | Static Pressure | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 47 | 68.6 | 89.4 | 117.1 | 160.9
24 | Total Pressure Adj | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 50.7 | 53.2 | 74.8 | 95.6 | 123.3 | 167.1
25 | SWL Adj | 41.8 | 41.3 | 40.7 | 40 | 39.1 | 38.5 | 39.3 | 60.2 | - | - | -
26 | SPL Adj | 26.8 | 26.3 | 25.7 | 25 | 24.1 | 23.5 | 24.3 | 45.2 | - | - | -
27 | 250 mm Medium-Profile Connection Box | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200 | DN200
28 | Static Pressure | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 48.7 | 70.3 | 91.2 | 118.8 | 162.6
29 | Total Pressure | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 55.2 | 76.9 | 97.7 | 125.4 | 169.2
30 | SWL Adj | 43.3 | 42.7 | 42.1 | 41.4 | 40.6 | 40 | 40.7 | 61.6 | - | - | -
31 | SPL Adj | 28.3 | 27.7 | 27.1 | 26.4 | 25.6 | 25 | 25.7 | 46.6 | - | - | -
32 | 200 mm Low-Profile Connection Box | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250 | DN250
33 | Static Pressure | 57.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 50 | 71.6 | 92.4 | 120.1 | 163.9
34 | Total Pressure | 63.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 55.7 | 77.4 | 98.2 | 125.9 | 169.6
35 | SWL Adj | 47.1 | 46.5 | 45.9 | 45.2 | 44.4 | 43.8 | 44.6 | 65.4 | - | - | -
36 | SPL Adj | 32.1 | 31.5 | 30.9 | 30.2 | 29.4 | 28.8 | 29.6 | 50.4 | - | - | -
| Shading Rules | D0 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | D9 | D10
| 4w/3w/2w | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE |  | false = doesn't exist |  | 7.35 | 8.664
| High Pressure/Flow | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE |  | true=red
| Damper colour | 2 | 2 | 2 | 1 | 0 | 0 | 2 | 2 | 2 | 2 | 2
| Min Flow | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  | true = red
| rejection | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | true = gray
| ALL SHADED | D0: FALSE
| Cmax Centre < Cmin | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  | true=red
| Cmax Perimeter < Cmin | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | shade for any time Cmax < C min
| C min > Cmax | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | shade for any time Cmin > Cmax
| Cmax Centre vs C select | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Cmax Perim vs C Select | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Cmin vs C Select | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
| Cmax centre vs selected | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | true = red
| Cmax perim vs selected | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | shade for any time valid cells: C select > Cmax
| Cmin vs selected | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | shade for any time valid cells: C select < Cmin
| DN350 Pressure | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 1=orange,2=red
| Sound Power Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 |  | 1=orange,2=red
| DN250 Pressure | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 1=orange,2=red
| Sound Power Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 |  | 1=orange,2=red
| DN200 Pressure | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 1=orange,2=red
| Sound Power Level | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 2 | 2 | 2 | 2 |  | 1=orange,2=red
| Thin Border Condition | D1: Recommended Spigot
| H350 | D0: TRUE; D1: DN200
| H250 | D0: FALSE; D1: DN200; D2: Recommended Box: H250-DN200
| H200 | D0: TRUE; D1: DN250
| Recommended Box Text | D0: Recommended Box: H250-DN200
| Selected Box | D0: H250

## Data (hidden)
Neck Sizes | °±Δ
DN250
DN355
DN500
Recommended Door Setting | 5 | D5
Front Page Notes
max airflow | max 250 L/s
comfort criteria | Comfort criteria for specific flowrate of 2.9 L/s/m² (average diffuser spacing of 5.9 m) & room temperature of 23°C
* Values valid for diffuser with 250mm high box and recommended 50.7 mm spigot
250 mm high box (default based on flow rate)
DN200 mm (default)
Direction(front pg) | 4 Way (360°) selected in cell M9. Shipped door setting is 4-way; adjustable on site to 2-way or 3-way
Pressure | ¹ Motorised pressure control damper - static pressure controlled to ≤ 50 Pa
Motorised PCD
|  | recommended for Design Static Pressure > 30 Pa | Include motorised pressure control damper
| Motorised Pressure Control Damper (DMPC) | Motorised Pressure Control Damper (DMPC) | DMPC (max static pressure controlled to 50 Pa)
Discharge Direction |  |  |  |  | 4 Way (360°)
4 Way (360°) | 4w |  |  |  | 4 Way | 4w
3 Way (270°) | 3w | for installations adjacent to wall |  |  | 3 Way | 3w
2 Way (2×90°) | 2s | for installation in hallways and corridors |  |  | 13 | 2s
2 Way (1×180°) | 2a | for installation in corners |  |  | 14 | 2a
Ceiling or Free | 1 | (1 = ceiling; 2 = free)
ADPI display
95%
90%
80%
70%
V
95% | 0.2
90% | 0.25
85% | 0.27
80% | 0.29
70% | 0.33
Code Generator
Size | DN355
Door Setting
Radio Selection | 2
Face Shape
0 | <face> | please select a valid face shape
1 | S595 | □ 595 mm square face |  | □○ | ø
2 | SX | custom face size (contact Smartair)
3 | <face> | Invalid Selection: circular face only available for 'freely suspended' (Cell N23)
1 | S595 | □ 595 mm square face | Colour Red | FALSE
Discharge | 4w
Grey Circular Face | TRUE
Cylindrical Selected | FALSE
Optional On Board Sensors |  |  |  | Desc | Desc (short)
IAQ display text | IAQ sensor (select one)
| Select | Code | Name
0 | FALSE | S0 | No Optional On-Board Sensors
1 | TRUE | C | On-board IAQ Sensor | • On-board IAQ Sensor (CO₂ + RH) | • IAQ Sensor (CO₂ + RH)
2 | FALSE |  | On-board PIR Sensor
|  | SC |  | • On-board IAQ Sensor (CO₂ + RH) | Optional On-board sensors • IAQ Sensor (CO₂ + RH)
IAQ
| Select | Code | Description
| 1 | C | (CO₂ + RH)
| 2 | V | (VOC)
| 1 | C | (CO₂ + RH)
Wall stat type
Wall stat option display | Touch Screen Wall-Stat with Room Temp (Available mid-2026)
Select | Code | Description
1 | W0 | No Wall-Stat | • No wall stat selected
2 | WP | Push button Wall-Stat | • Push button Wall-Stat
3 | WT | Touch Screen Wall-Stat | • Touch Screen Wall-Stat
1 | W0 | No Wall-Stat | • No wall stat selected | • No wall stat selected
Wall stat options
|  | Select | Code | Description | • Room Temp
| 1 | FALSE |  | CO₂ & RH
| 2 | FALSE |  | VOC
| 3 | FALSE |  | PM2.5
• No wall stat selected • Room Temp
Colour | RAL9003 | 1
(summary) | RAL9003
Box Options
Type
| select | Code | Display | Text | Description Table
| 1 | F | Foam* | Foam box | C | Sheetmetal (Cyl.) | Cylindrical sheetmetal box
| 2 | M | Sheetmetal | Sheetmetal box | M | Sheetmetal | Sheetmetal box
| 1 | F | Foam* | Foam box | F | Foam | Foam box
[5 empty] | N/A | N/A | Invalid box selection
Box Type
| Default Selected |  |  | Boxes List Normal
1 | 250 |  |  | 350 | 250 | 200 | bespoke | bespoke cylindrical |  |  | Common Box Data
2 | 350 |  |  | 250 | 350 | 250 | N/A | N/A |  |  | Size | Code | Option Display | Code Full | description
3 | 200 |  |  | 200 | 200 | 350 | N/A | N/A |  |  | 200 | 200 | 200 mm high box | KF200 | 200 mm high box
4 | bespoke |  |  | bespoke | bespoke | bespoke | N/A | N/A |  |  | 250 | 250 | 250 mm high box | KF250 | 250 mm high box
[11 empty] | 300 | 300 | 300 mm high box | KF300 | 300 mm high box
|  |  |  | Boxes List for MPCD | [6 empty] | 350 | 350 | 350 mm high box | KF350 | 350 mm high box
1 | 300 |  |  | 400 | 350 | 300 | 250 | bespoke | bespoke cylindrical |  | 400 | 400 | 400 mm high box | KF400 | 400 mm high box
2 | 250 |  |  | 350 | 300 | 250 | 350 | N/A | N/A |  | bespoke | B | bespoke | KFB | Bespoke box (contact Smartair)
3 | 350 |  |  | N/A | 400 | 350 | N/A | N/A | N/A |  | bespoke cylindrical | C | bespoke cylindrical | KMC | Bespoke cylindrical box (contact Smartair)
4 | N/A |  |  | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A | N/A | KN/A | invalid box selection
Round Spigot Connection | FALSE
Box Selection
Radio Buttons | Size | Display | Code | comment
1 | 250 | 250 mm high box (default) | KF250 | 250 mm high box (default based on flow rate)
2 | 350 | 350 mm high box | KF350 | 350 mm high box
3 | 200 | 200 mm high box | KF200 | 200 mm high box
4 | bespoke | bespoke | KFB | Bespoke box (contact Smartair)
1 | 250 | 250 mm high box (default) | KF250 | 250 mm high box (default based on flow rate)
Spigot Size Selection
Spigot Table | 350 | 250 | 200 | bespoke cylindrical | bespoke | RoundSpigot | N/A
1 | 200 | 200 | 250 | 300 | 200 | 150 | bespoke
2 | 150 | 150 | 200 | 250 | 150 | N/A | N/A
3 | 250 | 250 | 300 | 200 | 100 | N/A | N/A
4 | bespoke | bespoke | bespoke | bespoke | bespoke | N/A | N/A
Recommended Box Normal | 200
Recommended Box MPCD | 300
Spigot Size Normal
Selection | 250 |  |  | Size | Size | Code | Selection Text | Comment
1 | 200 |  |  | 150 | DN150 | SD150 | DN150 | DN150 mm
2 | 150 |  |  | 200 | DN200 | SD200 | DN200 | DN200 mm
3 | 250 |  |  | 250 | DN250 | SD250 | DN250 | DN250 mm
4 | bespoke |  |  | 300 | DN300 | SD300 | DN300 | DN300 mm
|  |  |  | 350 | DN350 | SD350 | DN350 | DN350 mm
|  |  |  | 400 | DN400 | SD400 | DN400 | DN400 mm
|  |  |  | bespoke | bespoke | SDX | bespoke spigot | Bespoke spigot size (contact Smartair)
|  |  |  | N/A | N/A | SDN/A | N/A | Invalid spigot selection
Selection | Size | Size DN | Code | Selection Text | Comment
1 | 200 | DN200 | SD200 | DN200 (default) | DN200 mm (default)
2 | 150 | DN150 | SD150 | DN150 | DN150 mm
3 | 250 | DN250 | SD250 | DN250 | DN250 mm
4 | bespoke | bespoke | SDX | bespoke spigot | Bespoke spigot size (contact Smartair)
1 | 200 | DN200 | SD200 | DN200 (default) | DN200 mm (default)
Default Box | TRUE
Default Spigot | TRUE
Default Selected | TRUE
Insulation
| Select | Code | Description
| 1 | R1 | R1 insulation
| 2 | R2 | R2 insulation
| 1 | R1 | R1 insulation |  |  |  | SE | Side entry spigot
Display Text | Foam box with R1 insulation | [5 empty] | TE | Top entry spigot
[7 empty] | D0 | No pressure damper
Cylindrical SM | [6 empty] | DMPC | Motorised Pressure Control Damper
[7 empty] | DGPR | Gravity Pressure Relief Damper
| Selected | Code | Description
Top Entry Spigot | TRUE | TE | Top entry spigot
Spigot Selection Radio | 1
Side/Top | SE
Damper | D0
Spigot Selection | [7 empty] | Code | Selection Text | Entry | Pressure Damper | Note
|  | Code | Selection Text | Entry | Pressure Damper | Note |  | SE-D0 | Side entry spigot | Side entry spigot | No pressure damper | No pressure damper
| 1 | SE-D0 | Side entry spigot | Side entry spigot | No pressure damper | No pressure damper |  | TE-D0 | Top entry spigot | Top entry spigot | No pressure damper | No pressure damper
| 2 | TE-D0 | Top entry spigot | Top entry spigot | No pressure damper | No pressure damper |  | SE-DGPR | Side entry spigot with Gravity Pressure Relief Damper | Side entry spigot | Gravity Pressure Relief Damper | Gravity Pressure Relief Damper (side entry spigots only - lengthened spigot)
| 3 | SE-DGPR | Side entry spigot with Gravity Pressure Relief Damper | Side entry spigot | Gravity Pressure Relief Damper | Gravity Pressure Relief Damper (side entry spigots only - lengthened spigot) |  | D.N/A | N/A | Invalid spigot selection | Invalid spigot selection | Invalid spigot selection
| 4 | SE-DMSS | Side entry spigots with Motorised Supply Source Damper | Side entry spigots | Motorised Supply Source Damper | Motorised Supply Source Damper (dual spigots for corner office source selection) |  | D0 | No pressure damper |  | No pressure damper
Selection | 1 | SE-D0 | Side entry spigot | Side entry spigot | No pressure damper | No pressure damper |  | SE-DMSS | Side entry spigots with Motorised Supply Source Damper | Side entry spigots | Motorised Supply Source Damper | Motorised Supply Source Damper (dual spigots for corner office source selection)
Pressure damper
DMPC Selection | FALSE | No pressure damper | No pressure damper
Code SE | SE-D0 | Side entry
Code TE | TE-D0 | Top entry
Spigot Summary
Size | DN200 mm (default) side entry spigot
Entry | Side entry spigot
Presssure Damper | No pressure damper
Pressure Damper note | No pressure damper
Desc. Table
DGPR Selection | FALSE | [5 empty] | D0 | No pressure damper | No pressure damper
Damper Selection | 0 | [5 empty] | DGPR | Gravity Pressure Relief Damper | Gravity Pressure Relief Damper (side entry spigots only - lengthened spigot)
Selection Button | Spigot with Integrated Gravity Pressure Relief Damper | [5 empty] | DMPC | Motorised Pressure Control Damper | Motorised Pressure Control Damper (round spigots only - lengthened spigot)
[7 empty] | DN/A | N/A | Invalid box selection
[7 empty] | DMPC (N/A) | Motorised Pressure Control Damper N/A (round spigots only) | Motorised Pressure Control Damper (round spigots only) (invalid)
| Select | Code | Option Text | Description |  |  | D.N/A | Checkbox N/A (side entry only) | Invalid box selection
| 0 | D0 | No pressure damper | No pressure damper
Gravity Pressure Relief Damper (DGPR) | 1 | D.N/A | Checkbox N/A (side entry only) | Invalid spigot selection
Selection | 0 | D0 | No pressure damper | No pressure damper
DMPC available | FALSE
System Setup | [6 empty] | D0 | No pressure damper | No pressure damper
Selection | Code | Selection Text |  |  |  |  | DMPC | Checkbox N/A - Selected in Cell E16 | Motorised Pressure Control Damper (round spigots only - lengthened spigot)
1 | SDA | Standalone Diffuser |  |  |  |  | DGPR | Spigot with Integrated Gravity Pressure Relief Damper | Gravity Pressure Relief Damper (side entry spigots only - lengthened spigot)
2 | VSN | Vari-Smart Networked Diffuser |  |  |  |  | D.N/A | Checkbox N/A (side entry only) | Invalid spigot selection
3 | BCN | Networked Diffuser
3 | BCN | Networked Diffuser
Order Summary
Model | Size | Shape |  | Box | Spigot
SMARTEMP HSC-VS- | DN355- | S595- |  | KF250R1- | SD200
Accessories | Colour | Spigot Entry | On-board | Wall sensor | Colour
- | RAL9003- | SE-D0- | SC- | W0
Diffuser Code | SMARTEMP HSC-VS-DN355-S595-KF250R1-SD200
Accessories Code | -RAL9003-SE-D0-SC-W0
Order Code | SMARTEMP HSC-VS-DN355-S595-KF250R1-SD200-RAL9003-SE-D0-SC-W0
Summary
0 | Selection? | 5 |  |  | TEXT
1 | Door | D5
2 | Airflow @ 100% Damper and 40 Pa | 116 | L/s |  | 116 L/s @ 0.78 Pa (static); damper open to 2950%
3 | Max Airflow | 100 | L/s
4 | Selected Design Pressure | 40.0 | Pa |  | 40.0 Pa (VAV turndown to 30%)
5 | Damper Position at 100 L/s and 40 Pa | 0.78 | Pa |  | 0.78 Pa (turndown to 30%) @ ΔT(supply - room) = -12.0 K
6 | Static Pressure @ 100% Airflow [Pa] | 29.5 | % | 2950 | 2950%
7 | Selected Turndown to | 0.3 | % | 30
8 | Min Selected Airflow | 30 | L/s
9 | Min Permissible % Turndown to | 0.101 | L/s
10 | Min Permissible Airflow | 10.1 | Pa |  | 10.1 Pa
11 | Max ΔT (heating) - Centre Zone [K] | 12.9 | K |  | + 12.9 K
12 | Max ΔT (heating) - Perimeter [K] | 8.6 | K |  | + 8.6 K
13 | Max Centreline Distance (centre) [m] | 9.3 | m |  | 9.3 m
14 | Max Centreline Distance Perimeter [m] | 8.6 | m |  | 8.6 m
15 | Min Centreline Distance [m] | 2.5 | m |  | 2.5 m
16 | Min Permissible Diffuser Height [m] | 2.2 | m |  | 2.2 m
17 | Mean Room Air Velocity [m/s] | 0.12 | m/s
18 | Mean Draught Rating (DR) | 0.101
19 | Mean PPD | 0.06
20 | Satisfies PPD Category (ISO7730) | B
21 | PMV | < 0.2
22 | 350 mm High-Profile Connection Box | DN200 |  |  | H350-DN200
23 | Static Pressure | 44.5 | Pa |  | 116 L/s @ 44.5 Pa (static)
24 | Total Pressure Adj | 50.7 | Pa |  | 116 L/s @ 50.7 Pa (total)
25 | SWL Adj | 38.5 | db(A) |  | 38.5 db(A)
26 | SPL Adj | 23.5 | NC |  | 23.5 NC
27 | 250 mm Medium-Profile Connection Box | DN200 |  |  | H250-DN200
28 | Static Pressure | 46.2 | Pa |  | 116 L/s @ 46.2 Pa (static)
29 | Total Pressure | 52.8 | Pa |  | 116 L/s @ 52.8 Pa (total)
30 | SWL Adj | 40 | db(A) |  | 40.0 db(A)
31 | SPL Adj | 25 | NC |  | 25.0 NC
32 | 200 mm Low-Profile Connection Box | DN250 |  |  | H200-DN250
33 | Static Pressure | 47.5 | Pa |  | 116 L/s @ 47.5 Pa (static)
34 | Total Pressure | 53.3 | Pa |  | 116 L/s @ 53.3 Pa (total)
35 | SWL Adj | 43.8 | db(A) |  | 43.8 db(A)
36 | SPL Adj | 28.8 | NC |  | 28.8 NC
37 | 0 | 0
38
Selection & Input Values
ΔT | -12.0 | K
Diffuser Location | Closed Ceiling
Display Text
Noise | 2 | 3 | 4
Size | Pressure | db(A) | NC
350 | 116 L/s @ 44.5 Pa (static) | 38.5 db(A) | 23.5 NC
250 | 116 L/s @ 46.2 Pa (static) | 40.0 db(A) | 25.0 NC
200 | 116 L/s @ 47.5 Pa (static) | 43.8 db(A) | 28.8 NC
250 | 116 L/s @ 46.2 Pa (static) | 40.0 db(A) | 25.0 NC
250 | 116 L/s @ 46.2 Pa (static) | 40.0 db(A) | 25.0 NC |  | Recommended Box
Diagram
| Cmin | Cmax (Centre) | Cmax (Perimeter)
| 2.5 m | 9.3 m | 8.6 m
C Nominal
C select | 5.9 m
C Max = 9.3 m/8.6 m (centre/perimeter zone)
C Min = 2.5 m
C Nominal = 5.9 m
room box | Nominal Specific Airflow Rate = 2.9 L/s/m² | Nominal
Selected Diffuser Height = 2.7 m
Min Recommended Diffuser Height = 2.2 m
Specific Flowrate | 2.9 L/s/m²
Top Box 1 | C Max = 9.3 m/8.6 m (centre/perimeter zone)
box 2 | C Min = 2.5 m | 1 | Specific Airflow Rate @ Average C = 2.9 L/s/m²
box 3 | C Nominal = 5.9 m | 2 | Specific Airflow Rate @ Selected C = 2.9 L/s/m²
TEXT
ADPI | 90 |  | ≥ 90%
Room Temp | 23 |  | 23 °C
Mean Room Air Velocity [m/s] | 0.12 |  | 0.12 m/s
Mean Draught Rating (DR) | 10.1 |  | 10.1% @ room temperature of 23 °C
Mean PPD | 6 |  | 6%
Satisfies PPD Category (ISO7730) | B |  | Category B
PMV | 0.2 |  | -0.2 < PMV < +0.2
rec. box height | H250 [mm]
rec. box spigot | DN200 [mm]
Description | Summary sentence | With newline char and formatting
HSC-VS Diffuser
| Recommended D5 door setting (adjusted on-site) | • Recommended D5 door setting (adjusted on-site)
| Standard On-Board Sensors • Supply Temperature • Room Temperature • Supply Pressure | Standard On-Board Sensors • Supply Temperature • Room Temperature • Supply Pressure Optional On-board sensors • IAQ Sensor (CO₂ + RH)
HMI Options • No wall stat selected • Room Temp
| 4 Way (360°) discharge | • 4 Way (360°) discharge |  |  | Connection Box Details
| □ 595 mm square face | • □ 595 mm square face |  |  | • 250 mm high box (default) | 250 mm high box (default)
| Powder coated to RAL9003 | • Powder coated to RAL9003 |  |  | • Foam box with R1 insulation | Foam box with R1 insulation
| 250 mm high box (default based on flow rate) |  |  |  | • DN200 mm (default) side entry spigot | DN200 mm (default) side entry spigot
| Foam box with R1 insulation |  |  |  | • No pressure damper | No pressure damper
DN200 mm (default) side entry spigot
| No pressure damper |  | •
| Diffuser Setup | Aux
FOR DISPLAY | HSC-VS Diffuser • Recommended D5 door setting (adjusted on-site) • 4 Way (360°) discharge • □ 595 mm square face • Powder coated to RAL9003 | Standard On-Board Sensors • Supply Temperature • Room Temperature • Supply Pressure Optional On-board sensors • IAQ Sensor (CO₂ + RH) | HMI Options • No wall stat selected • Room Temp | Standard On-Board Sensors • Supply Temperature • Room Temperature • Supply Pressure Optional On-board sensors • IAQ Sensor (CO₂ + RH) HMI Options • No wall stat selected • Room Temp | Connection Box Details • 250 mm high box (default) • Foam box with R1 insulation • DN200 mm (default) side entry spigot • No pressure damper
Summary Page | HSC-VS Diffuser • Recommended D5 door setting (adjusted on-site) • 4 Way (360°) discharge • □ 595 mm square face • Powder coated to RAL9003 Connection Box Details • 250 mm high box (default) • Foam box with R1 insulation • DN200 mm (default) side entry spigot • No pressure damper
Connection Box
| 200 mm Ultra Low Profile Connection Box |  |  |  | Round Spigot | Ovalised Spigot |  |  | Max Airflow @ 3.5 m/s Effective Spigot Velocity [L/s]
|  | Box Height | Spigot Clearance |  | Spigot Diameter | Spigot Height | Spigot Width | Spigot Area [m2] |  | Ovalised
|  | H₁ | H₂ | H₄ | Ø₁ | H₃ | L₃
H200-DN150 | DN150 | 200 | 50 | 25 | 0 | 125 | 170 | 0.016654 | 59 | TRUE
H200-DN200 | DN200 | 200 | 50 | 25 | 0 | 125 | 252 | 0.024754 | 87 | TRUE
H200-DN250 | DN250 | 200 | 50 | 25 | 0 | 125 | 329 | 0.03232 | 114 | TRUE
H200-DN300 | DN300 | 200 | 50 | 25 | 0 | 125 | 404 | 0.039658 | 139 | TRUE
H250-DN150 | DN150 | 250 | 50 | 51 | 149 | 0 | 0 | 0.017437 | 62 | FALSE
H250-DN200 | DN200 | 250 | 50 | 25 | 0 | 175 | 220 | 0.030293 | 107 | TRUE
H250-DN250 | DN250 | 250 | 50 | 25 | 0 | 175 | 306 | 0.042 | 147 | TRUE
H250-DN300 | DN300 | 250 | 50 | 25 | 0 | 175 | 385 | 0.052908 | 186 | TRUE
H250-DN350 | DN350 | 250 | 50 | 25 | 0 | 175 | 461 | 0.06343 | 223 | TRUE
H350-DN150 | DN150 | 350 | 50 | 151 | 149 | 0 | 0 | 0.017437 | 62 | FALSE
H350-DN200 | DN200 | 350 | 50 | 101 | 199 | 0 | 0 | 0.031103 | 109 | FALSE
H350-DN250 | DN250 | 350 | 50 | 51 | 249 | 0 | 0 | 0.048695 | 171 | FALSE
H350-DN300 | DN300 | 350 | 50 | 50 | 0 | 250 | 341 | 0.066961 | 235 | TRUE
H350-DN350 | DN350 | 350 | 50 | 50 | 0 | 250 | 426 | 0.083559 | 293 | TRUE
H400-DN300 | DN300 | 400 | 50 | 51 | 299 | 0 | 0 | 0.070215 | 245.7538 | FALSE
H400-DN300 | DN300 | 400
bespoke | bespoke | bespoke | 50 | - | - | - | - | - |  | FALSE
N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | FALSE
Column Number | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
H250-DN200 | DN200 | 250 | 50 | 25 | 0 | 175 | 220 | 0.030293 | 107 | TRUE
DISPLAY |  | H₁ | H₂ | H₄ | H₃ | L₃
|  | 250 | 50 | 25 | 175 | 220 | [mm]
Spigot Velocity | 3.3 m/s | 3.3 | m/s
1

## Notes
SMARTEMP PRODUCT SELECTION CALCULATOR
Helical Vari-Swirl Diffuser - Notes
More detailed information available in the HSC-VS product brochure
DIFFUSER NOTES
1. Diffusers are shipped with their VAV dampers set to D0. Suitable adjustment to the door setting is recommended by the diffuser microprocessor during on-site air balancing.
2. Shipped door setting is 4-way; adjustable on site to 2-way or 3-way
3. Vari-Smart Controller (VSC): VSCs may, additionally, be required to provide central control of the HSC-VS diffusers served by the associated AHU/FCU and to optimise AHU/FCU supply air pressure (fan speed) and supply air temperature (cooling/heating valve) control.
SELECTION NOTES
ΔT -ve denotes cooling
ΔT +ve denotes heating
NOISE & ACOUSTICS
Sound Pressure Level [NC] describes the noise level perceived by a listener 2.1 m from a diffuser located at 2.7 to 3.0 m height in a 70 m3 space (typical office) with 10 dB(A) room absorption that is uniformly distributed, due to the sound power level generated by that single diffuser only. Additional diffusers add additional noise logarithmically (eg. a second diffuser of the same sound power level as the first adds NC 3 to the sound pressure level perceived by the listener).
Sound Pressure Level is provided as a guide only for a standard, carpeted single office with acoustic ceiling. An acoustical engineer should be consulted for detailed calculations, especially for applications with more than one diffuser or where hard surfaces are involved.
HOW TO SELECT
Index Diffuser - Set 'Design Airflow Rate' to determine 'Door Setting' and 'Desired Design Pressure'
[5 empty] | Select: | [5 empty] | Non-Index Diffusers - Set 'Design Airflow Rate' and the Duct-Determined 'Design Static Pressure' to determine 'Door Setting'
[7 empty] | Design Airflow Rate | 145 | L/s (desired flow rate)
[5 empty] | Results: | [5 empty] | Select:
[7 empty] | SMARTEMP HSC-VS- | D2 |  |  |  |  | Design Airflow Rate | 150 | L/s (desired flow rate)
[7 empty] | P1: Static Pressure @ Design Airflow & 100% Damper | 26.1 | Pa (pressure required to run index diffuser at 100% open) |  |  |  | Design Static Pressure | 46.1 | Pa (from step 3)
Result:
[13 empty] | SMARTEMP HSC-VS- | D3 | (recommend selecting 'Door Setting' with the largest 'Damper Position')
| Repeat Steps 3 & 4 | [11 empty] | Damper Position at 150 L/s and 46.1 Pa | 82%
| Calculate: | P = Pstart - Ploss
|  | P = 56.1 - 10.0 - 10.0 - 5.0 = 31.1 Pa | [8 empty] | Note: The design pressure, and hence the noise, of all remaining diffusers will be less than the 'highest pressure diffuser'. It is therefore generally not necessary to calculate these.
Select:
|  |  | Design Airflow Rate | 155 | L/s (desired flow rate)
|  |  | Design Static Pressure | 31.1 | Pa
| Result: | [12 empty] | Highest Pressure Diffuser (Closest to AHU) - Calculate Diffuser Design Static Pressure
|  |  | SMARTEMP HSC-VS- | D2
|  |  | Damper Position at 155 L/s and 31.1 Pa | 97% | [9 empty] | P3 = P2 - P flex loss
P3 = 56.1 - 10
P3 = 46.1 Pa
All balancing dampers to be fully open
Calculate First Takeoff Static Pressure
P2 = index run pressure loss
P2 = P1 + P flex loss 2 + P duct loss 1
P2 = 26.1 + 20 + 10
P2 = 56.1 Pa
SENSORS
On-Board Sensors |  |  |  |  | Optional Wall Stat
standard | room temperature |  |  |  | Push Button Wall Stat |  |  | Touch Screen Wall Stat
| supply temperature |  |  |  | standard | room temperature sensor |  | standard | room temperature sensor
| pressure sensor | [6 empty] | optional (select multiple) | CO2 & RH
optional | IAQ Sensor - select one: | [7 empty] | VOC
| CO2 & RH, or | [7 empty] | PM2.5
VOC
PIR Sensor
SYSTEM SETUP
Stand-Alone: Each HSC-VS diffuser is suitable to operate stand-alone (requires 24 VDC power supply). · No Wall-Stat: Diffuser commissioning and air balancing requires micro-USB connection of a laptop, programmed with commissioning tools, to the diffuser hub; or · Wall-Stat: An optional wall-stat (push-button or touchscreen) wired to the diffuser allows setpoint adjustment by the user, and direct diffuser commissioning and air balancing. · BMS Linked: A Modbus RS485 comms chain may optionally link stand-alone HSC-VS diffusers (with or without a wall-stat) to a BMS / central controller (by others) to allow diffuser sensors to be monitored and/or set-points to be changed remotely, and to provide laptop network access for commissioning and air balancing via a Smartair Commissioning App.
Networked: A Modbus RS465 comms chain is required to link HSC-VS diffusers as for “BMS Linked” operation above (with or without wall-stat); plus AHU/FCU control and system optimisation by the Vari-Swirl diffuser system via one of two options: · 1. Central Controls by Others: a third-party BMS / central controller is supplied and programmed by others to provide simplified AHU/FCU control (a “Central Controls by Others” functional description is available from Smartair Diffusion); or · 2. Vari-Smart Controller (VSC): a VSC (optionally connected to a BMS) is available from Fusion Modulair™, pre-programmed to aggregate HSC-VS preferences and dynamically reset and optimise requests for AHU/FCU cooling/heating mode, supply air temperature, and supply air pressure or fan speed. System supply air pressure and supply air temperature optimisation saves fan energy by targeting operation with at least one HSC-VS damper fully open, and dynamically balances fan energy savings, dehumidification, contaminant flushing, comfort, and zone over-cooling/heating mitigation. Advanced features include supply air temperature trim-and-respond control with importance multiplier zone priority weighting, zone type (priority, executive, meeting, office, public), economy and comfort settings (optionally user-adjustable, including user-boost functions), active / setback operation (manual / scheduled / PIR operated), optimum start/stop sequences, integrated commissioning and air balancing tools, and robustness to operational errors (over-pressure relief; sensor drift mitigation, automatic fault detection, and nuisance-alarm prevention).
Standalone |  |  |  |  | Standalone - BMS Linked |  |  |  |  | Networked Diffuser with Central Controller (by others) | [6 empty] | Networked Diffuser with Vari-Smart Controller (VSC)
Each diffuser acts independently |  |  |  |  | Each diffuser acts independently |  |  |  |  | BMS (by others) | [6 empty] | Vari-Smart controller
BMS contractor responsible for fan/temperature control |  |  |  |  | BMS contractor responsible for fan/temperature control |  |  |  |  | Vari-Swirl controls programming (by others) based on Functional Description by Smartair Diffusion | [6 empty] | Zoning programmed through Vari-Smart Controller
[5 empty] | Comms: MODBUS RS485 (daisy chain) |  |  |  |  | Comms: MODBUS RS485 (daisy chain) | [6 empty] | Comms: MODBUS TCP/IP
more detailed information available in the HSC-VS product brochure
LAYOUT AND DISCHARGE PATTERN
Max and Min Centreline Distance is to be halved for spacing to walls or glazing.
|  | 4 Way (360°) | [6 empty] | 3 Way (270°) |  |  |  | 2 Way (2×90°) |  |  |  |  | 2 Way (1×180°)
• | default |  |  |  |  | • | for installations adjacent to walls |  |  |  | • | for installations in corridors |  |  |  | • | for installations in corners
• | use when D > Cmin/2 |  |  |  |  | • | use when D < Cmin/2 |  |  |  | • | use when D < Cmin/2 |  |  |  | • | use when D < Cmin/2
• | available for D0 to D10 |  |  |  |  | • | available for D1 to D10 |  |  |  | • | available for D2 to D10 |  |  |  | • | available for D2 to D10
| Legend: |  | Active Door
|  |  | Closed Door | [6 empty] | Plan View

## Connection Box Details
SMARTEMP PRODUCT SELECTION CALCULATOR
Helical Vari-Swirl Diffuser - Connection Box Details
The standard connection box is side-entry rigid PU foam, R1 insulated. The side-entry spigot is removable. Options include R2 foam, a removable spigot with either an integrated motorised pressure control damper (MPCD)* or a gravity pressure relief damper (GPRD)* * refer to 'Optional Pressure Dampers' tab
Connection Box Details (R1 Insulated) without optional pressure dampers*
ASNZ nominal sizes
200 mm Low-Profile connection Box |  |  |  | Round Spigot | Ovalised Spigot |  |  | Airflow @ 3.5 m/s Effective Spigot Velocity [L/s]
| Box Height | Spigot Clearance |  | Spigot Diameter | Spigot Height | Spigot Width | Spigot Area [m2]
| H1 | H2 | H4 | Ø1 | H3 | L3
DN150 | 200 | 50 | 25 |  | 125 | 170 | 0.016654 | 59
DN200 | 200 | 50 | 25 |  | 125 | 252 | 0.024754 | 87
DN250 | 200 | 50 | 25 |  | 125 | 329 | 0.03232 | 114
DN300 | 200 | 50 | 25 |  | 125 | 404 | 0.039658 | 139
250 mm Medium-Profile connection Box |  |  |  | Round Spigot | Ovalised Spigot |  |  | Airflow @ 3.5 m/s Effective Spigot Velocity [L/s]
| Box Height | Spigot Clearance |  | Spigot Diameter | Spigot Height | Spigot Width | Spigot Area [m2] |  |  | Circular Spigot
| H1 | H2 | H4 | Ø1 | H3 | L3
DN150 | 250 | 50 | 51 | 149 |  |  | 0.017437 | 62
DN200 | 250 | 50 | 25 |  | 175 | 220 | 0.030293 | 107
DN250 | 250 | 50 | 25 |  | 175 | 306 | 0.042 | 147 |  |  | ALL DIMENSIONS IN mm
DN300 | 250 | 50 | 25 |  | 175 | 385 | 0.052908 | 186
DN350 | 250 | 50 | 25 |  | 175 | 461 | 0.06343 | 223
350 mm High-Profile connection Box |  |  |  | Round Spigot | Ovalised Spigot |  |  | Airflow @ 3.5 m/s Effective Spigot Velocity [L/s]
| Box Height | Spigot Clearance |  | Spigot Diameter | Spigot Height | Spigot Width | Spigot Area [m2]
| H1 | H2 | H4 | Ø1 | H3 | L3
DN150 | 350 | 50 | 151 | 149 |  |  | 0.017437 | 62
DN200 | 350 | 50 | 101 | 199 |  |  | 0.031103 | 109 |  | Ovalised Spigot
DN250 | 350 | 50 | 51 | 249 |  |  | 0.048695 | 171
DN300 | 350 | 50 | 50 |  | 250 | 341 | 0.066961 | 235
DN350 | 350 | 50 | 50 |  | 250 | 426 | 0.083559 | 293
Plan View

## Optional Pressure Dampers
SMARTEMP PRODUCT SELECTION CALCULATOR
Helical Vari-Swirl Diffuser - Connection Box Details (with optional Motorised Pressure Control Damper)
Connection Box with Motorised Pressure Control Damper
350 mm High-Profile connection Box |  |  |  |  | Round Spigot |  | Airflow @ 3.5 m/s Effective Spigot Velocity [L/s]
| Box Height | Spigot Clearance |  |  | Spigot Diameter | Spigot Area [m2]
| H1 | H2 | H4 | L1 | Ø1
DN150 | 250 | 100 | 400 | 116 | 149 | 0.017437 | 61.0282
DN200 | 300 |  |  | 98 | 199 | 0.031103 | 108.8589
DN250 | 350 |  |  | TBC | 249 | 0.048695 | 170.4342
DN300 | 400 |  |  | TBC | 299 | 0.070215 | 245.7538
Motorised Pressure Control Damper

## Selection Summary & Print
| HSC-VS Performance Calculator Summary |  |  | HSC-VS Performance Calculator Summary
Project | <Project Name> |  | Selected Box | H₁ | H₂ | H₄ | H₃ | L₃ |  | Spigot Velocity
Company | <Name> |  | H250-DN200 | 250 | 50 | 25 | 175 | 220 | [mm] | 3.3 m/s
Client | <Name>
Product | SMARTEMP HSC-VS-DN355
Electronic Vari-Swirl Diffuser
Summary
Recommended Door Setting | D5 | see note 1
Disharge Pattern | 4 Way (360°) | see note 2
Selected Airflow ¹ | 116 L/s @ 0.78 Pa (static); damper open to 2950%
Min Selected Airflow | 40.0 Pa (VAV turndown to 30%)
Min Permissible Airflow | 0.78 Pa (turndown to 30%) @ ΔT(supply - room) = -12.0 K
Max Heating ΔT (Centre Zone) | + 12.9 K |  | Selection
Max Heating ΔT (Perimeter Zone) | + 8.6 K | ¹ Values valid for diffuser with recommended connection box H350-DN200 | Diffuser Configuration | HSC-VS Diffuser • Recommended D5 door setting (adjusted on-site) • 4 Way (360°) discharge • □ 595 mm square face • Powder coated to RAL9003 Connection Box Details • 250 mm high box (default) • Foam box with R1 insulation • DN200 mm (default) side entry spigot • No pressure damper
¹ Motorised pressure control damper - static pressure controlled to ≤ 50 Pa
Acoustic Performance
Sound Power Level ¹ | 40.0 db(A)
Sound Pressure Level ^¹ | 25.0 NC | ^ based on 10dB room absorption
Comfort Performance
Selected ADPI Target | ≥ 90%
Mean Room Air Velocity | 0.12 m/s
Draught Rating (DR) | 10.1% @ room temperature of 23 °C
PPD | 6% |  | Sensors | Standard On-Board Sensors • Supply Temperature • Room Temperature • Supply Pressure Optional On-board sensors • IAQ Sensor (CO₂ + RH) |  |  |  | HMI Options • No wall stat selected • Room Temp
Satisfies PPD | Category B | (ISO7730)
Satisfies PMV | -0.2 < PMV < +0.2 | (ISO7730; ASHRAE Std 55)
Recommended Layout
Diffuser Location | Closed Ceiling
C Max = 9.3 m/8.6 m (centre/perimeter zone) |  | Selected Diffuser Height = 2.7 m
C Min = 2.5 m |  | Min Recommended Diffuser Height = 2.2 m | Order Code (select to copy)
C Nominal = 5.9 m |  |  | SMARTEMP HSC-VS-DN355-S595-KF250R1-SD200-RAL9003-SE-D0-SC-W0
Nominal Specific Airflow Rate = 2.9 L/s/m² |  |  | Diffuser | SMARTEMP HSC-VS-DN355-S595-KF250R1-SD200
|  |  | Accessories | -RAL9003-SE-D0-SC-W0
Notes
1. Diffusers are shipped with their VAV dampers set to D0. Suitable adjustment to the door setting is recommended by the diffuser microprocessor during on-site air balancing.
2. Shipped door setting is 4-way; adjustable on site to 2-way or 3-way
3. Vari-Smart Controller (VSC): VSCs may, additionally, be required to provide central control of the HSC-VS diffusers served by the associated AHU/FCU and to optimise AHU/FCU supply air pressure (fan speed) and supply air temperature (cooling/heating valve) control.
v 4.1 [01/2026]

## NEWCMAX (hidden)
HSC-VS-DN355-D0
Max Airflow | 220 | L/s
Turndown To | 15 | % | Use Turndown %
Use Turndown L/s
ΔT | -15 | K
HSC-FD-DN355-R0
Max Airflow | 220 | L/s
Turndown To | 15 | %
ΔT | -15 | K
|  | Select v' for Cmax |  |  |  |  | f_TD (Sliding Scale) |  | f_P (Sliding Scale)
HSC-VS |  | 95% | 90% | 80% | 70%
factor (TD) |  | 0.535 | 0.535 | 0.535 | 0.535 |  | TD | Factor | Pressure | Factor
factor (P) |  | 0.75 | 0.75 | 0.75 | 0.75 |  | 100% | 1 | 30 | 0.75
v' perimeter |  | 1.27 | 1 | 0.7 | 0.5 | datum v' equivalent to HSC-FD | 30% | 0.535 | 5 | 1
actual v' perim | @-12K | 0.50959 | 0.40125 | 0.28087 | 0.20062 |  | Absolute Min | 0.535 | Factor | 0.75
v' centre |  | 1.01 | 0.808 | 0.538 | 0.451 | datum v' equivalent to HSC-FD | Factor | 0.535
actual v' centre | @-12K | 0.40526 | 0.32421 | 0.21587 | 0.18096
Results Table for 2.7m |  | Cmax
| Turndown (L/s) | 95% | 90% | 80% | 70%
HSC-VS Perimeter | 33 | 7.1977 | 8.1114 | 9.6949 | 11.4712
VS v' (L/s/m2) |  | 0.63698 | 0.50156 | 0.35109 | 0.25078
HSC-FD Perimeter | 33 | 4.4423 | 5.0052 | 6.1657 | 7.2968
v' (L/s/m2) |  | 1.3378 | 1.0538 | 0.69444 | 0.49583
HSC-VS Centre | 33 | 8.0711 | 9.0238 | 11.0587 | 12.0783
VS v' (L/s/m2) |  | 0.50658 | 0.40526 | 0.26984 | 0.2262
HSC-FD Centre | 33 | 4.9755 | 5.5682 | 6.8218 | 7.4358
v' (L/s/m2) |  | 1.0664 | 0.85147 | 0.56729 | 0.47747
|  |  | 0.808 | 0.76857 | 0.902
|  |  | 0.89889 | 0.87668 | 0.94974
|  |  | 0.89889 | 0.87668 | 0.94974
Vmin option | 1
HSC-FD
Vmax | Vmin
221 | 66.3
Vtd | 33 | L/s
Cmax Table Perimeter
adpi | v' @Vmax | v' @ Vmin | v' | Cmax
95% | 0.955 | 1.27 | 1.3378 | 4.4423
90% | 0.75 | 1 | 1.0538 | 5.0052
80% | 0.5 | 0.66 | 0.69444 | 6.1657
70% | 0.35 | 0.47 | 0.49583 | 7.2968
v' & Vmax
v' & Vmin
Cmax Centre Zone
adpi | v' @Vmax | v' @ Vmin | v' | Cmax
95% | 0.75963 | 1.0121 | 1.0664 | 4.9755
90% | 0.60762 | 0.80827 | 0.85147 | 5.5682
80% | 0.40294 | 0.53818 | 0.56729 | 6.8218
70% | 0.33072 | 0.45147 | 0.47747 | 7.4358
v' & Vmax
v' & Vmin
HSC-VS
Pressure | 30
Vmin | 33 | L/s
TD % | 15%
|  |  | ADPI FACTORS of 90% |  | F'
adpi | v' @Vmax | v' @ Vmin | Vmax | Vmin (check)
95% | 0.955 | 1.27 | 1.2733 | 0.7874 | 0.88619
90% | 0.75 | 1 | 1 | 1 | 1
80% | 0.5 | 0.66 | 0.66667 | 1.5152 | 1.2247
70% | 0.35 | 0.47 | 0.46667 | 2.1277 | 1.4639

## dimensions old (hidden)
ASNZ nominal sizes
200 mm Ultra Low Profile Plenum Box |  |  |  | Round Spigot | Ovalised Spigot |  |  |  | Max Airflow @ 3.0 m/s Effective Spigot Velocity [L/s]
| Box Height | Spigot Clearance |  | Spigot Diameter | Spigot Height | Spigot End Radius | Spigot Width | Spigot Area [m2]
| H1 | H2 | H4 | Ø1 | H3 | R2 | L1
DN150 | 200 | 50 | 25 |  | 125 | 62.5 | 163 | 0.016984 | 50.9527
DN200 | 200 | 50 | 25 |  | 125 | 62.5 | 241 | 0.026802 | 80.4051
DN250 | 200 | 50 | 25 |  | 125 | 62.5 | 320 | 0.036619 | 109.8576
DN300 | 200 | 50 | 25 |  | 125 | 62.5 | 398 | 0.046437 | 139.31
250 mm Low Profile Plenum Box |  |  |  | Round Spigot | Ovalised Spigot |  |  |  | Max Airflow @ 3.0 m/s Effective Spigot Velocity [L/s]
| Box Height | Spigot Clearance |  | Spigot Diameter | Spigot Height | Spigot End Radius | Spigot Width | Spigot Area [m2]
| H1 | H2 | H4 | Ø1 | H3 | R2 | L1
DN150 | 250 | 61 | 40 | 149 |  |  |  | 0.017437 | 52.3099
DN200 | 250 | 61 | 38 |  | 151 | 75.5 | 226 | 0.029293 | 87.879
DN250 | 250 | 41 | 33 |  | 176 | 88 | 291 | 0.044487 | 133.4614
DN300 | 250 | 50 | 50 |  | 150 | 75 | 384 | 0.052779 | 158.3363
DN350 | 250 | 50 | 50 |  | 150 | 75 | 463 | 0.06456 | 193.6792
300 mm High Profile Plenum Box |  |  |  | Round Spigot | Ovalised Spigot |  |  |  | Max Airflow @ 3.0 m/s Effective Spigot Velocity [L/s]
| Box Height | Spigot Clearance |  | Spigot Diameter | Spigot Height | Spigot End Radius | Spigot Width | Spigot Area [m2]
| H1 | H2 | H4 | Ø1 | H3 | R2 | L1
DN150 | 300 | 61 | 90 | 149 |  |  |  | 0.017437 | 52.3099
DN200 | 300 | 51 | 50 | 199 |  |  |  | 0.031103 | 93.3077
DN250 | 300 | 66 | 34 |  | 200 | 100 | 275 | 0.046496 | 139.4867
DN300 | 300 | 56 | 43 |  | 201 | 100.5 | 355 | 0.062672 | 188.0173
DN350 | 300 | 50 | 70 |  | 180 | 90 | 445 | 0.078226 | 234.677
400 mm High Profile Plenum Box |  |  |  | Round Spigot | Ovalised Spigot |  |  |  | Max Airflow @ 3.0 m/s Effective Spigot Velocity [L/s]
| Box Height | Spigot Clearance |  | Spigot Diameter | Spigot Height | Spigot End Radius | Spigot Width | Spigot Area [m2]
| H1 | H2 | H4 | Ø1 | H3 | R2 | L1
DN300 | 400 | 51 | 50 | 299 |  |  |  | 0.070215 | 210.6461
DN350 | 400 | 56 | 42 |  | 302 | 151 | 377 | 0.093898 | 281.693
DN400 | 400 | 51 | 47 |  | 302 | 151 | 454 | 0.11765 | 352.9391

## layout diagrams (hidden)
Selection | 4w
4w
3w
2s
2a